## base_case
Bus
ID | Zone | kV Base | V sol [pu] | Ang sol [deg] | Vmin [pu] | Vmax [pu] | P Gen [MW] | Q Gen [MVAR] | P Load [MW] | Q Load [MVAR] | P motor [MW] | Q motor [MVAR] | P shunt [MW] | Q shunt [MVAR]
B1 | 0 | 345 | 1.021 | 3.4 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B10 | 0 | 345 | 0.956 | 3.2 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B11 | 0 | 345 | 0.952 | 1.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B12 | 0 | 138 | 0.932 | 2.3 | 0.9 | 1.1 | 0 | 0 | 7.5 | 88 | 0 | 0 | 0 | 0
B13 | 0 | 345 | 0.953 | 2.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B14 | 0 | 345 | 0.952 | 2.1 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B15 | 0 | 345 | 0.954 | 5.2 | 0.9 | 1.1 | 0 | 0 | 320 | 153 | 0 | 0 | 0 | 0
B16 | 0 | 345 | 0.973 | 8.3 | 0.9 | 1.1 | 0 | 0 | 329 | 32.3 | 0 | 0 | 0 | 0
B17 | 0 | 345 | 0.98 | 5.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B18 | 0 | 345 | 0.98 | 3.9 | 0.9 | 1.1 | 0 | 0 | 158 | 30 | 0 | 0 | 0 | 0
B19 | 0 | 345 | 0.977 | 20 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B2 | 0 | 345 | 1.018 | 4.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B20 | 0 | 230 | 0.973 | 23.2 | 0.9 | 1.1 | 0 | 0 | 628 | 103 | 0 | 0 | 0 | 0
B21 | 0 | 345 | 0.984 | 10.9 | 0.9 | 1.1 | 0 | 0 | 274 | 115 | 0 | 0 | 0 | 0
B22 | 0 | 345 | 1.015 | 15.7 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B23 | 0 | 345 | 1.013 | 15.5 | 0.9 | 1.1 | 0 | 0 | 247.5 | 84.6 | 0 | 0 | 0 | 0
B24 | 0 | 345 | 0.983 | 8.4 | 0.9 | 1.1 | 0 | 0 | 308.6 | -92.2 | 0 | 0 | 0 | 0
B25 | 0 | 345 | 1.029 | 6.6 | 0.9 | 1.1 | 0 | 0 | 224 | 47.2 | 0 | 0 | 0 | 0
B26 | 0 | 345 | 1.013 | 6.5 | 0.9 | 1.1 | 0 | 0 | 139 | 17 | 0 | 0 | 0 | 0
B27 | 0 | 345 | 0.992 | 4.9 | 0.9 | 1.1 | 0 | 0 | 281 | 75.5 | 0 | 0 | 0 | 0
B28 | 0 | 345 | 1.017 | 10.3 | 0.9 | 1.1 | 0 | 0 | 206 | 27.6 | 0 | 0 | 0 | 0
B29 | 0 | 345 | 1.019 | 13.2 | 0.9 | 1.1 | 0 | 0 | 283.5 | 26.9 | 0 | 0 | 0 | 0
B3 | 0 | 345 | 0.984 | 2.1 | 0.9 | 1.1 | 0 | 0 | 322 | 2.4 | 0 | 0 | 0 | 0
B30 | 0 | 16.5 | 1.048 | 7.2 | 0.9 | 1.1 | 250 | 170.19 | 0 | 0 | 0 | 0 | 0 | 0
B31 | 0 | 16.5 | 0.982 | 0 | 0.9 | 1.1 | 69.43 | 128.42 | 9.2 | 4.6 | 0 | 0 | 0 | 0
B32 | 0 | 16.5 | 0.983 | 11.1 | 0.9 | 1.1 | 650 | 163.63 | 0 | 0 | 0 | 0 | 0 | 0
B33 | 0 | 16.5 | 0.997 | 25.1 | 0.9 | 1.1 | 615 | 138.16 | 0 | 0 | 0 | 0 | 0 | 0
B34 | 0 | 16.5 | 1.012 | 33.7 | 0.9 | 1.1 | 1016 | 261.11 | 0 | 0 | 0 | 0 | 0 | 0
B35 | 0 | 16.5 | 1.049 | 20.7 | 0.9 | 1.1 | 650 | 262.58 | 0 | 0 | 0 | 0 | 0 | 0
B36 | 0 | 16.5 | 1.064 | 23.5 | 0.9 | 1.1 | 560 | 224.55 | 0 | 0 | 0 | 0 | 0 | 0
B37 | 0 | 16.5 | 1.028 | 13.4 | 0.9 | 1.1 | 540 | 14.76 | 0 | 0 | 0 | 0 | 0 | 0
B38 | 0 | 16.5 | 1.026 | 20.3 | 0.9 | 1.1 | 830 | 57.22 | 0 | 0 | 0 | 0 | 0 | 0
B39 | 0 | 345 | 1.03 | 0.4 | 0.9 | 1.1 | 1000 | 294.08 | 1104 | 250 | 0 | 0 | 0 | 0
B4 | 0 | 345 | 0.947 | -0.7 | 0.9 | 1.1 | 0 | 0 | 500 | 184 | 0 | 0 | 0 | 0
B5 | 0 | 345 | 0.949 | -1.2 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B6 | 0 | 345 | 0.95 | -0.9 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B7 | 0 | 345 | 0.942 | -2.9 | 0.9 | 1.1 | 0 | 0 | 233.8 | 84 | 0 | 0 | 0 | 0
B8 | 0 | 345 | 0.943 | -3.3 | 0.9 | 1.1 | 0 | 0 | 522 | 176 | 0 | 0 | 0 | 0
B9 | 0 | 345 | 1.006 | -1.1 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generator
ID | Bus ID | DBase ID | Type | Rated S [MVA] | kV Nominal | Generator Type | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | Q max. [MVAR] | Q min. [MVAR] | Ctrled BusID | Ctrld Bus/V [pu]
G10 | B30 | G10 | Generator | 1000 | 16.5 | PV | 250 | 170.19 | 302.43 | 82.7 | 2.887 | 560 | -240 | B30 | 1.048
G01 | B39 | G01 | Generator | 10000 | 345 | PV | 1000 | 294.08 | 1042.34 | 95.9 | 10.12 | 5600 | -2400 | B39 | 1.03
G02 | B31 | G02 | Generator | 700 | 16.5 | SW | 69.43 | 128.42 | 145.98 | 47.6 | 1.487 | 392 | -168 | B31 | 0.982
G03 | B32 | G03 | Generator | 800 | 16.5 | PV | 650 | 163.63 | 670.28 | 97 | 6.818 | 448 | -192 | B32 | 0.983
G04 | B33 | G04 | Generator | 800 | 16.5 | PV | 615 | 138.16 | 630.33 | 97.6 | 6.321 | 448 | -192 | B33 | 0.997
G05 | B34 | G05 | Generator | 600 | 16.5 | PV | 1016 | 261.11 | 1049.02 | 96.9 | 10.363 | 672 | -288 | B34 | 1.012
G06 | B35 | G06 | Generator | 800 | 16.5 | PV | 650 | 262.58 | 701.03 | 92.7 | 6.681 | 448 | -192 | B35 | 1.049
G07 | B36 | G07 | Generator | 700 | 16.5 | PV | 560 | 224.55 | 603.34 | 92.8 | 5.673 | 392 | -168 | B36 | 1.064
G08 | B37 | G08 | Generator | 700 | 16.5 | PV | 540 | 14.76 | 540.2 | 100 | 5.256 | 392 | -168 | B37 | 1.028
G09 | B38 | G09 | Generator | 1000 | 16.5 | PV | 830 | 57.22 | 831.97 | 99.8 | 8.105 | 560 | -240 | B38 | 1.026
Static Load
ID | Bus ID | DBase ID | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%]
S10 | B21 | S10 | 274 | 115 | 297.15 | 92.2
S01 | B3 | S01 | 322 | 2.4 | 322.01 | 100
S11 | B23 | S11 | 247.5 | 84.6 | 261.56 | 94.6
S02 | B4 | S02 | 500 | 184 | 532.78 | 93.8
S12 | B24 | S12 | 308.6 | -92.2 | 322.08 | 95.8
S03 | B7 | S03 | 233.8 | 84 | 248.43 | 94.1
S13 | B25 | S13 | 224 | 47.2 | 228.92 | 97.9
S04 | B8 | S04 | 522 | 176 | 550.87 | 94.8
S14 | B26 | S14 | 139 | 17 | 140.04 | 99.3
S05 | B12 | S05 | 7.5 | 88 | 88.32 | 8.5
S15 | B27 | S15 | 281 | 75.5 | 290.97 | 96.6
S06 | B15 | S06 | 320 | 153 | 354.7 | 90.2
S16 | B28 | S16 | 206 | 27.6 | 207.84 | 99.1
S07 | B16 | S07 | 329 | 32.3 | 330.58 | 99.5
S17 | B29 | S17 | 283.5 | 26.9 | 284.77 | 99.6
S08 | B18 | S08 | 158 | 30 | 160.82 | 98.2
S18 | B31 | S18 | 9.2 | 4.6 | 10.29 | 89.4
S09 | B20 | S09 | 628 | 103 | 636.39 | 98.7
S19 | B39 | S19 | 1104 | 250 | 1131.95 | 97.5
Branch
ID | Bus From | Bus To | DBase ID | Type | kV Nominal | Length | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | I angle [deg] | P losses [MW] | Q losses [MVAR] | Ampacity (Norm.) [pu] | Loading % | Ampacity (Emer.) [pu] | Loading(Emer) %
L10 | B5 | B8 | L10 | Line | 345 | 75.1 | 290.2 | 25.01 | 291.28 | 99.6 | 3.07 | -6.2 | 0.75 | -2.61 | 4.78 | 64.2 | 7.171 | 42.8
L20 | B15 | B16 | L20 | Line | 345 | 63 | -546.92 | -134 | 563.1 | -97.1 | 5.903 | 171.4 | 3.11 | 16.67 | 10.756 | 54.9 | 11.951 | 49.4
L30 | B25 | B26 | L30 | Line | 345 | 216.5 | 10.91 | 19.96 | 22.75 | 48 | 0.221 | -54.7 | 0.07 | -52.77 | 4.78 | 4.6 | 7.171 | 3.1
L11 | B6 | B7 | L11 | Line | 345 | 61.7 | 355.39 | 57.76 | 360.06 | 98.7 | 3.789 | -10.1 | 0.87 | 3.15 | 4.78 | 79.3 | 7.171 | 52.8
L21 | B16 | B17 | L21 | Line | 345 | 59.7 | 463.25 | -108.01 | 475.67 | 97.4 | 4.889 | 21.4 | 1.66 | 8.34 | 10.756 | 45.5 | 11.951 | 40.9
L31 | B26 | B27 | L31 | Line | 345 | 98.5 | 202.58 | 119.34 | 235.12 | 86.2 | 2.32 | -24 | 0.79 | -15.74 | 4.78 | 48.5 | 7.171 | 32.4
L12 | B6 | B11 | L12 | Line | 345 | 55 | -519.88 | 28.77 | 520.68 | -99.8 | 5.48 | -177.7 | 2.1 | 12.1 | 10.756 | 50.9 | 11.951 | 45.9
L22 | B16 | B19 | L22 | Line | 345 | 130.7 | -973.01 | 146.13 | 983.92 | -98.9 | 10.112 | -163.1 | 16.47 | 171.42 | 10.756 | 94 | 11.951 | 84.6
L32 | B26 | B28 | L32 | Line | 345 | 317.7 | -140.84 | -30.06 | 144.02 | -97.8 | 1.421 | 174.5 | 0.83 | -71.21 | 4.78 | 29.7 | 7.171 | 19.8
L13 | B7 | B8 | L13 | Line | 345 | 30.8 | 120.73 | -29.39 | 124.25 | 97.2 | 1.318 | 10.7 | 0.07 | -6.15 | 4.78 | 27.6 | 7.171 | 18.4
L23 | B16 | B21 | L23 | Line | 345 | 90.5 | -326.81 | -63.07 | 332.84 | -98.2 | 3.421 | 177.4 | 0.92 | -8.79 | 4.78 | 71.6 | 7.171 | 47.7
L33 | B26 | B29 | L33 | Line | 345 | 418.9 | -189.9 | -33.54 | 192.84 | -98.5 | 1.903 | 176.5 | 2.02 | -84.1 | 4.78 | 39.8 | 7.171 | 26.5
L14 | B8 | B9 | L14 | Line | 345 | 243.3 | -111.89 | -171.63 | 204.88 | -54.6 | 2.172 | 119.8 | 0.95 | -21.3 | 4.78 | 45.4 | 7.171 | 30.3
L24 | B16 | B24 | L24 | Line | 345 | 39.5 | -42.46 | -158.02 | 163.63 | -26 | 1.682 | 113.4 | 0.08 | -4.9 | 4.78 | 35.2 | 7.171 | 23.5
L34 | B28 | B29 | L34 | Line | 345 | 101.2 | -347.68 | 13.54 | 347.94 | -99.9 | 3.422 | -167.5 | 1.65 | -8.05 | 4.78 | 71.6 | 7.171 | 47.7
L15 | B9 | B39 | L15 | Line | 345 | 167.6 | -112.84 | -150.33 | 187.96 | -60 | 1.868 | 125.8 | 0.2 | -119.29 | 4.78 | 39.1 | 7.171 | 26
L25 | B17 | B18 | L25 | Line | 345 | 55 | 382.21 | -27.61 | 383.21 | 99.7 | 3.911 | 9.9 | 1.06 | -0.14 | 4.78 | 81.8 | 7.171 | 54.5
L16 | B10 | B11 | L16 | Line | 345 | 28.8 | 509 | 33.48 | 510.1 | 99.8 | 5.338 | -0.6 | 1.14 | 5.63 | 10.756 | 49.6 | 11.951 | 44.7
L26 | B17 | B27 | L26 | Line | 345 | 116 | 79.37 | -88.74 | 119.06 | 66.7 | 1.215 | 54 | 0.16 | -29.16 | 4.78 | 25.4 | 7.171 | 16.9
L17 | B10 | B13 | L17 | Line | 345 | 28.8 | 138.67 | 37.2 | 143.58 | 96.6 | 1.503 | -11.8 | 0.09 | -5.66 | 4.78 | 31.4 | 7.171 | 21
L27 | B21 | B22 | L27 | Line | 345 | 93.8 | -601.73 | -169.28 | 625.09 | -96.3 | 6.354 | 175.2 | 3.21 | 30.31 | 7.971 | 79.7 | 11.951 | 53.2
L18 | B13 | B14 | L18 | Line | 345 | 67.7 | 116.88 | -2.9 | 116.92 | 100 | 1.227 | 4.3 | 0.14 | -14.11 | 4.78 | 25.7 | 7.171 | 17.1
L28 | B22 | B23 | L28 | Line | 345 | 64.3 | 43.1 | -0.87 | 43.11 | 100 | 0.425 | 16.9 | 0.01 | -18.8 | 4.78 | 8.9 | 7.171 | 5.9
L19 | B14 | B15 | L19 | Line | 345 | 145.4 | -225.91 | -1.95 | 225.91 | -100 | 2.374 | -178.4 | 1.02 | -20.95 | 4.78 | 49.7 | 7.171 | 33.1
L29 | B23 | B24 | L29 | Line | 345 | 234.6 | 353.98 | 70.36 | 360.91 | 98.1 | 3.561 | 4.2 | 2.84 | 9.43 | 4.78 | 74.5 | 7.171 | 49.7
L1 | B1 | B2 | L1 | Line | 345 | 275.5 | -217.51 | 80.13 | 231.8 | -93.8 | 2.271 | -156.4 | 2.04 | -67 | 4.78 | 47.5 | 7.171 | 31.7
L2 | B1 | B39 | L2 | Line | 345 | 167.6 | 217.51 | -80.13 | 231.8 | 93.8 | 2.271 | 23.6 | 0.47 | -67.1 | 4.78 | 47.5 | 7.171 | 31.7
L3 | B2 | B3 | L3 | Line | 345 | 101.2 | 326.5 | 192.57 | 379.06 | 86.1 | 3.725 | -25.7 | 1.87 | -4.05 | 4.78 | 77.9 | 7.171 | 52
L4 | B2 | B25 | L4 | Line | 345 | 57.6 | -296.56 | 109.67 | 316.19 | -93.8 | 3.107 | -154.9 | 6.87 | -6.84 | 4.78 | 65 | 7.171 | 43.3
L5 | B3 | B4 | L5 | Line | 345 | 142.8 | 225.18 | 150.15 | 270.65 | 83.2 | 2.751 | -31.6 | 1.03 | -3.8 | 4.78 | 57.5 | 7.171 | 38.4
L6 | B3 | B18 | L6 | Line | 345 | 89.1 | -222.55 | 44.07 | 226.88 | -98.1 | 2.306 | -166.7 | 0.6 | -13.4 | 4.78 | 48.2 | 7.171 | 32.2
L7 | B4 | B5 | L7 | Line | 345 | 85.8 | 65.77 | -21.21 | 69.1 | 95.2 | 0.73 | 17.2 | 0.04 | -11.41 | 4.78 | 15.3 | 7.171 | 10.2
L8 | B4 | B14 | L8 | Line | 345 | 86.5 | -341.61 | -8.84 | 341.73 | -100 | 3.607 | 177.8 | 1.04 | 4.32 | 4.78 | 75.5 | 7.171 | 50.3
L9 | B5 | B6 | L9 | Line | 345 | 17.4 | -224.48 | -34.81 | 227.16 | -98.8 | 2.394 | 169.9 | 0.11 | -2.43 | 5.976 | 40.1 | 8.963 | 26.7
Transformer
TXFO ID | Bus From | Bus To | DBase ID | Type | Rated S [MVA] | kV Nominal Primary | kV Nominal Secondary | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | Iangle [deg] | P losses [MW] | Q losses [MVAR] | Capacity (Norm.) [MVA] | Loading [%] Capacity | Capacity (Emer.) [MVA] | Loading [%] Capacity | Tap Ratio % | Tap Pos [%] | Min | Max | Setpoint Min | Setpoint Max | Ctrld Bus/V [pu] | Ctrled BusID
Tap Pos [%]
T10 | B2 | B30 | T10 | Fixed-Tap Xmer | 1000 | 345 | 16.5 | -249.5 | -155.1 | 293.78 | -84.9 | 2.887 | 152.9 | 0.5 | 15.09 | 1100 | 26.7 | 1150 | 25.5 | 100 | 100
T01 | B12 | B11 | T01 | Fixed-Tap Xmer | 300 | 138 | 345 | 14.16 | -43.47 | 45.72 | 31 | 0.491 | 74.2 | 0.04 | 1.05 | 500 | 9.1 | 550 | 8.3 | 100 | 100
T11 | B29 | B38 | T11 | Fixed-Tap Xmer | 1000 | 345 | 16.5 | -824.74 | 45.26 | 825.99 | -99.8 | 8.105 | -163.7 | 5.26 | 102.48 | 1100 | 75.1 | 1150 | 71.8 | 100 | 100
T02 | B12 | B13 | T02 | Fixed-Tap Xmer | 300 | 138 | 345 | -21.66 | -44.53 | 49.52 | -43.7 | 0.531 | 118.2 | 0.05 | 1.23 | 500 | 9.9 | 550 | 9 | 100 | 100
T12 | B19 | B20 | T12 | Fixed-Tap Xmer | 1000 | 345 | 230 | -377.27 | 56.15 | 381.43 | -98.9 | 3.904 | -151.5 | 1.07 | 21.03 | 1100 | 34.7 | 1150 | 33.2 | 100 | 100
T03 | B6 | B31 | T03 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -60.1 | -118.9 | 133.23 | -45.1 | 1.402 | 115.9 | 0.13 | 4.91 | 800 | 16.7 | 850 | 15.7 | 100 | 100
T04 | B10 | B32 | T04 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -647.68 | -70.68 | 651.52 | -99.4 | 6.818 | 177 | 2.32 | 92.94 | 900 | 72.4 | 950 | 68.6 | 100 | 100
T05 | B19 | B33 | T05 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -612.2 | -81.45 | 617.6 | -99.1 | 6.321 | -167.6 | 2.8 | 56.72 | 900 | 68.6 | 950 | 65 | 100 | 100
T06 | B20 | B34 | T06 | Fixed-Tap Xmer | 600 | 230 | 16.5 | -1006.34 | -67.88 | 1008.62 | -99.8 | 10.363 | -160.7 | 9.66 | 193.23 | 1400 | 72 | 1500 | 67.2 | 100 | 100
T07 | B22 | B35 | T07 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -648.04 | -198.72 | 677.83 | -95.6 | 6.681 | 178.7 | 1.95 | 63.86 | 900 | 75.3 | 950 | 71.4 | 100 | 100
T08 | B23 | B36 | T08 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -558.39 | -137.02 | 574.96 | -97.1 | 5.673 | -178.3 | 1.61 | 87.53 | 800 | 71.9 | 850 | 67.6 | 100 | 100
T09 | B25 | B37 | T09 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -538.34 | 49.34 | 540.6 | -99.6 | 5.256 | -168.1 | 1.66 | 64.1 | 800 | 67.6 | 850 | 63.6 | 100 | 100
Abnormal Report
ID
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L30 | B25 | B26 | 0.221 | 2.39
L21 | B16 | B17 | 4.889 | 5.378
L31 | B26 | B27 | 2.32 | 2.39
L32 | B26 | B28 | 1.421 | 2.39
L13 | B7 | B8 | 1.318 | 2.39
L33 | B26 | B29 | 1.903 | 2.39
L14 | B8 | B9 | 2.172 | 2.39
L24 | B16 | B24 | 1.682 | 2.39
L15 | B9 | B39 | 1.868 | 2.39
L16 | B10 | B11 | 5.338 | 5.378
L26 | B17 | B27 | 1.215 | 2.39
L17 | B10 | B13 | 1.503 | 2.39
L18 | B13 | B14 | 1.227 | 2.39
L28 | B22 | B23 | 0.425 | 2.39
L19 | B14 | B15 | 2.374 | 2.39
L1 | B1 | B2 | 2.271 | 2.39
L2 | B1 | B39 | 2.271 | 2.39
L6 | B3 | B18 | 2.306 | 2.39
L7 | B4 | B5 | 0.73 | 2.39
L9 | B5 | B6 | 2.394 | 2.988
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B2 | B30 | 293.781 | 550
T01 | B12 | B11 | 45.717 | 250
T02 | B12 | B13 | 49.517 | 250
T12 | B19 | B20 | 381.429 | 550
T03 | B6 | B31 | 133.228 | 400
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]
Summary Report
LOAD FLOW STUDY PARAMETERS
Study : |  |  | UNTITLED
Time : |  |  | Fri Jul 23 11h58m46s 2021
Method : |  |  | Newton-Raphson
Constraints : |  |  | Not applied
Flat start : |  |  | Yes
Tcul txfo used as fixed tap : |  |  | n\a
Block Q-flow Txfo Adjustment |  |  | n\a
Block P-flow Txfo Adjustment : |  |  | n\a
Block Switchable Shunt Adjustment : |  |  | n\a
Block DC Link Adjustment : |  |  | n\a
Base power : |  |  | 100.00 [MVA]
Tolerance : |  |  | 0.100 [MVA]
COMPLETE SUMMARY REPORT
Summary Data |  |  |  |  | Active Power |  | Reactive Power
Total generation |  |  |  |  | 6180.425 |  | 1714.694
Spinning reserve |  |  |  |  | 9209.574
Static Load |  |  |  |  | 6097.1 |  | 1408.9
Shunt loads |  |  |  |  | 0 |  | 0
Motor loads |  |  |  |  | 0 |  | 0
Total load |  |  |  |  | 6097.1 |  | 1408.9
Line / cable losses |  |  |  |  | 56.292 |  | -398.367
Transformer losses |  |  |  |  | 27.034 |  | 704.162
Total losses |  |  |  |  | 83.326 |  | 305.795
Mismatches |  |  |  |  | 0 |  | -0.001

## induction_motor+HVDC
Bus
ID | Zone | kV Base | V sol [pu] | Ang sol [deg] | Vmin [pu] | Vmax [pu] | P Gen [MW] | Q Gen [MVAR] | P Load [MW] | Q Load [MVAR] | P motor [MW] | Q motor [MVAR] | P shunt [MW] | Q shunt [MVAR]
B1 | 0 | 345 | 0.996 | -33.3 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B10 | 0 | 345 | 0.9 | -14.6 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B11 | 0 | 345 | 0.888 | -14.7 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B12 | 0 | 138 | 0.869 | -15.6 | 0.9 | 1.1 | 0 | 0 | 7.5 | 88 | 0 | 0 | 0 | 0
B13 | 0 | 345 | 0.894 | -16.3 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B14 | 0 | 345 | 0.89 | -20.6 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B15 | 0 | 345 | 0.909 | -26.1 | 0.9 | 1.1 | 0 | 0 | 320 | 153 | 0 | 0 | 0 | 0
B16 | 0 | 345 | 0.936 | -26.4 | 0.9 | 1.1 | 0 | 0 | 329 | 32.3 | 0 | 0 | 0 | 0
B17 | 0 | 345 | 0.947 | -27.9 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B18 | 0 | 345 | 0.945 | -28.7 | 0.9 | 1.1 | 0 | 0 | 158 | 30 | 0 | 0 | 0 | 0
B19 | 0 | 345 | 0.964 | -14 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B2 | 0 | 345 | 1.001 | -29.6 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B20 | 0 | 230 | 0.966 | -10.8 | 0.9 | 1.1 | 0 | 0 | 628 | 103 | 0 | 0 | 0 | 0
B21 | 0 | 345 | 0.946 | -27.2 | 0.9 | 1.1 | 0 | 0 | 274 | 115 | 0 | 0 | 0 | 0
B22 | 0 | 345 | 0.973 | -25.7 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B23 | 0 | 345 | 0.94 | -28.3 | 0.9 | 1.1 | 0 | 0 | 247.5 | 84.6 | 800 | 600 | 0 | 0
B24 | 0 | 345 | 0.941 | -27.7 | 0.9 | 1.1 | 0 | 0 | 308.6 | -92.2 | 0 | 0 | 0 | 0
B25 | 0 | 345 | 1.016 | -27.8 | 0.9 | 1.1 | 0 | 0 | 224 | 47.2 | 0 | 0 | 0 | 0
B26 | 0 | 345 | 0.996 | -27.6 | 0.9 | 1.1 | 0 | 0 | 139 | 17 | 0 | 0 | 0 | 0
B27 | 0 | 345 | 0.967 | -29 | 0.9 | 1.1 | 0 | 0 | 281 | 75.5 | 0 | 0 | 0 | 0
B28 | 0 | 345 | 1.008 | -23.8 | 0.9 | 1.1 | 0 | 0 | 206 | 27.6 | 0 | 0 | 0 | 0
B29 | 0 | 345 | 1.013 | -20.8 | 0.9 | 1.1 | 0 | 0 | 283.5 | 26.9 | 0 | 0 | 0 | 0
B3 | 0 | 345 | 0.947 | -28.7 | 0.9 | 1.1 | 0 | 0 | 322 | 2.4 | 0 | 0 | 0 | 0
B30 | 0 | 16.5 | 1.048 | -27.2 | 0.9 | 1.1 | 250 | 264.86 | 0 | 0 | 0 | 0 | 0 | 0
B31 | 0 | 16.5 | 0.982 | 0 | 0.9 | 1.1 | 899.72 | 548.19 | 9.2 | 4.6 | 0 | 0 | 0 | 0
B32 | 0 | 16.5 | 0.983 | -6.3 | 0.9 | 1.1 | 650 | 439.65 | 0 | 0 | 0 | 0 | 0 | 0
B33 | 0 | 16.5 | 0.997 | -8.7 | 0.9 | 1.1 | 632 | 232.17 | 0 | 0 | 0 | 0 | 0 | 0
B34 | 0 | 16.5 | 1.012 | -0.1 | 0.9 | 1.1 | 1016 | 304.82 | 0 | 0 | 0 | 0 | 0 | 0
B35 | 0 | 16.5 | 1.049 | -20.6 | 0.9 | 1.1 | 650 | 570.16 | 0 | 0 | 0 | 0 | 0 | 0
B36 | 0 | 16.5 | 1.064 | -19.7 | 0.9 | 1.1 | 560 | 515.17 | 0 | 0 | 0 | 0 | 0 | 0
B37 | 0 | 16.5 | 1.028 | -20.9 | 0.9 | 1.1 | 540 | 69.04 | 0 | 0 | 0 | 0 | 0 | 0
B38 | 0 | 16.5 | 1.026 | -13.7 | 0.9 | 1.1 | 830 | 97.13 | 0 | 0 | 0 | 0 | 0 | 0
B39 | 0 | 345 | 1.03 | -41.9 | 0.9 | 1.1 | 1000 | 617.7 | 1104 | 250 | 0 | 0 | 0 | 0
B39_REC | 0 | 100 | 1.016 | -43.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B4 | 0 | 345 | 0.877 | -22.8 | 0.9 | 1.1 | 0 | 0 | 500 | 184 | 0 | 0 | 0 | 0
B5 | 0 | 345 | 0.86 | -16.3 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B6 | 0 | 345 | 0.867 | -14.9 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B7 | 0 | 345 | 0.833 | -16.5 | 0.9 | 1.1 | 0 | 0 | 233.8 | 84 | 0 | 0 | 0 | 0
B8 | 0 | 345 | 0.822 | -16.4 | 0.9 | 1.1 | 0 | 0 | 522 | 176 | 0 | 0 | 0 | 0
B9 | 0 | 345 | 0.725 | 1.6 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B9_INV | 0 | 100 | 0.713 | 5.6 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generator
ID | Bus ID | DBase ID | Type | Rated S [MVA] | kV Nominal | Generator Type | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | Q max. [MVAR] | Q min. [MVAR] | Ctrled BusID | Ctrld Bus/V [pu]
G10 | B30 | G10 | Generator | 1000 | 16.5 | PV | 250 | 264.86 | 364.21 | 68.6 | 3.477 | 560 | -240 | B30 | 1.048
G01 | B39 | G01 | Generator | 10000 | 345 | PV | 1000 | 617.7 | 1175.4 | 85.1 | 11.412 | 5600 | -2400 | B39 | 1.03
G02 | B31 | G02 | Generator | 700 | 16.5 | SW | 899.72 | 548.19 | 1053.57 | 85.4 | 10.729 | 392 | -168 | B31 | 0.982
G03 | B32 | G03 | Generator | 800 | 16.5 | PV | 650 | 439.65 | 784.72 | 82.8 | 7.982 | 448 | -192 | B32 | 0.983
G04 | B33 | G04 | Generator | 800 | 16.5 | PV | 632 | 232.17 | 673.3 | 93.9 | 6.752 | 448 | -192 | B33 | 0.997
G05 | B34 | G05 | Generator | 600 | 16.5 | PV | 1016 | 304.82 | 1060.74 | 95.8 | 10.478 | 2 | -2 | B34 | 1.012
G06 | B35 | G06 | Generator | 800 | 16.5 | PV | 650 | 570.16 | 864.63 | 75.2 | 8.24 | 448 | -192 | B35 | 1.049
G07 | B36 | G07 | Generator | 700 | 16.5 | PV | 560 | 515.17 | 760.92 | 73.6 | 7.155 | 392 | -168 | B36 | 1.064
G08 | B37 | G08 | Generator | 700 | 16.5 | PV | 540 | 69.04 | 544.4 | 99.2 | 5.297 | 392 | -168 | B37 | 1.028
G09 | B38 | G09 | Generator | 1000 | 16.5 | PV | 830 | 97.13 | 835.66 | 99.3 | 8.141 | 560 | -240 | B38 | 1.026
Motor
ID | Bus ID | DBase ID | Type | V sol [pu] | S [MVA] | P. Factor [%] | I [pu]
IM1 | B23 | IM1 | Induction Motor | 0.94 | 1000 | 80 | 10.641
Static Load
ID | Bus ID | DBase ID | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%]
S10 | B21 | S10 | 274 | 115 | 297.15 | 92.2
S01 | B3 | S01 | 322 | 2.4 | 322.01 | 100
S11 | B23 | S11 | 247.5 | 84.6 | 261.56 | 94.6
S02 | B4 | S02 | 500 | 184 | 532.78 | 93.8
S12 | B24 | S12 | 308.6 | -92.2 | 322.08 | 95.8
S03 | B7 | S03 | 233.8 | 84 | 248.43 | 94.1
S13 | B25 | S13 | 224 | 47.2 | 228.92 | 97.9
S04 | B8 | S04 | 522 | 176 | 550.87 | 94.8
S14 | B26 | S14 | 139 | 17 | 140.04 | 99.3
S05 | B12 | S05 | 7.5 | 88 | 88.32 | 8.5
S15 | B27 | S15 | 281 | 75.5 | 290.97 | 96.6
S06 | B15 | S06 | 320 | 153 | 354.7 | 90.2
S16 | B28 | S16 | 206 | 27.6 | 207.84 | 99.1
S07 | B16 | S07 | 329 | 32.3 | 330.58 | 99.5
S17 | B29 | S17 | 283.5 | 26.9 | 284.77 | 99.6
S08 | B18 | S08 | 158 | 30 | 160.82 | 98.2
S18 | B31 | S18 | 9.2 | 4.6 | 10.29 | 89.4
S09 | B20 | S09 | 628 | 103 | 636.39 | 98.7
S19 | B39 | S19 | 1104 | 250 | 1131.95 | 97.5
Branch
ID | Bus From | Bus To | DBase ID | Type | kV Nominal | Length | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | I angle [deg] | P losses [MW] | Q losses [MVAR] | Ampacity (Norm.) [pu] | Loading % | Ampacity (Emer.) [pu] | Loading(Emer) %
L10 | B5 | B8 | L10 | Line | 345 | 75.1 | 35.89 | 287.02 | 289.26 | 12.4 | 3.362 | -99.1 | 0.93 | 2.7 | 4.78 | 70.3 | 7.171 | 46.9
L20 | B15 | B16 | L20 | Line | 345 | 63 | 25.91 | -263.26 | 264.54 | 9.8 | 2.909 | 58.3 | 0.72 | -7.01 | 10.756 | 27 | 11.951 | 24.3
L30 | B25 | B26 | L30 | Line | 345 | 216.5 | -5.05 | 38.63 | 38.95 | -13 | 0.383 | -125.2 | 0.13 | -50.6 | 4.78 | 8 | 7.171 | 5.3
L11 | B6 | B7 | L11 | Line | 345 | 61.7 | 235.1 | 300.46 | 381.5 | 61.6 | 4.4 | -66.9 | 1.18 | 9.95 | 4.78 | 92 | 7.171 | 61.4
L21 | B16 | B17 | L21 | Line | 345 | 59.7 | 255.37 | -138.61 | 290.56 | 87.9 | 3.106 | 2.1 | 0.66 | -3.46 | 10.756 | 28.9 | 11.951 | 26
L31 | B26 | B27 | L31 | Line | 345 | 98.5 | 186.42 | 168.86 | 251.52 | 74.1 | 2.526 | -69.7 | 0.95 | -13.09 | 4.78 | 52.8 | 7.171 | 35.2
L12 | B6 | B11 | L12 | Line | 345 | 55 | -47.86 | -217.71 | 222.91 | -21.5 | 2.571 | 87.5 | 0.44 | -5.51 | 10.756 | 23.9 | 11.951 | 21.5
L22 | B16 | B19 | L22 | Line | 345 | 130.7 | -987.93 | 40.15 | 988.74 | -99.9 | 10.569 | 156 | 17.93 | 190.69 | 11.951 | 88.4 | 12.549 | 84.2
L32 | B26 | B28 | L32 | Line | 345 | 317.7 | -140.98 | -46.67 | 148.51 | -94.9 | 1.491 | 134.1 | 0.86 | -68.79 | 4.78 | 31.2 | 7.171 | 20.8
L13 | B7 | B8 | L13 | Line | 345 | 30.8 | 0.11 | 206.51 | 206.51 | 0.1 | 2.478 | -106.4 | 0.25 | -2.44 | 10.756 | 23 | 11.951 | 20.7
L23 | B16 | B21 | L23 | Line | 345 | 90.5 | 90.44 | -86.2 | 124.94 | 72.4 | 1.335 | 17.3 | 0.13 | -20.41 | 4.78 | 27.9 | 7.171 | 18.6
L33 | B26 | B29 | L33 | Line | 345 | 418.9 | -189.61 | -49.96 | 196.09 | -96.7 | 1.969 | 137.7 | 2.07 | -81.16 | 4.78 | 41.2 | 7.171 | 27.5
L14 | B8 | B9 | L14 | Line | 345 | 243.3 | -487.18 | 317.28 | 581.39 | -83.8 | 7.074 | -163.3 | 11.84 | 163.2 | 10.756 | 65.8 | 11.951 | 59.2
L24 | B16 | B24 | L24 | Line | 345 | 39.5 | 338.31 | -103.89 | 353.9 | 95.6 | 3.783 | -9.3 | 0.43 | 2.42 | 4.78 | 79.1 | 7.171 | 52.8
L34 | B28 | B29 | L34 | Line | 345 | 101.2 | -347.84 | -5.48 | 347.89 | -100 | 3.452 | 155.3 | 1.67 | -7.43 | 4.78 | 72.2 | 7.171 | 48.1
L25 | B17 | B18 | L25 | Line | 345 | 55 | 158.84 | -3.68 | 158.88 | 100 | 1.678 | -26.6 | 0.2 | -9.49 | 4.78 | 35.1 | 7.171 | 23.4
L16 | B10 | B11 | L16 | Line | 345 | 28.8 | 76.41 | 247.38 | 258.91 | 29.5 | 2.877 | -87.4 | 0.34 | -2.18 | 10.756 | 26.8 | 11.951 | 24.1
L26 | B17 | B27 | L26 | Line | 345 | 116 | 95.86 | -131.46 | 162.7 | 58.9 | 1.719 | 26 | 0.33 | -25.02 | 4.78 | 36 | 7.171 | 24
L17 | B10 | B13 | L17 | Line | 345 | 28.8 | 570.41 | 64.88 | 574.09 | 99.4 | 6.38 | -21.1 | 1.63 | 11.66 | 10.756 | 59.3 | 11.951 | 53.4
L27 | B21 | B22 | L27 | Line | 345 | 93.8 | -183.69 | -180.79 | 257.73 | -71.3 | 2.725 | 108.3 | 0.56 | -13.84 | 7.971 | 34.2 | 11.951 | 22.8
L18 | B13 | B14 | L18 | Line | 345 | 67.7 | 588.94 | -0.39 | 588.94 | 100 | 6.584 | -16.3 | 3.9 | 30.08 | 10.756 | 61.2 | 11.951 | 55.1
L28 | B22 | B23 | L28 | Line | 345 | 64.3 | 462.78 | 306.07 | 554.84 | 83.4 | 5.704 | -59.2 | 1.99 | 14.9 | 7.171 | 79.6 | 9.561 | 59.7
L19 | B14 | B15 | L19 | Line | 345 | 145.4 | 348.85 | -104.38 | 364.13 | 95.8 | 4.09 | -3.9 | 2.94 | 5.89 | 4.78 | 85.6 | 7.171 | 57
L29 | B23 | B24 | L29 | Line | 345 | 234.6 | -29.26 | -17.48 | 34.09 | -85.8 | 0.363 | 120.8 | 0.02 | -31.58 | 4.78 | 7.6 | 7.171 | 5.1
L1 | B1 | B2 | L1 | Line | 345 | 275.5 | -609.4 | 152.48 | 628.19 | -97 | 6.31 | 160.7 | 14.33 | -30.64 | 10.756 | 58.7 | 11.951 | 52.8
L2 | B1 | B39 | L2 | Line | 345 | 167.6 | 609.4 | -152.48 | 628.19 | 97 | 6.31 | -19.3 | 3.88 | 20.05 | 10.756 | 58.7 | 11.951 | 52.8
L3 | B2 | B3 | L3 | Line | 345 | 101.2 | -62.38 | 350.11 | 355.63 | -17.5 | 3.552 | -129.7 | 1.76 | -4.01 | 4.78 | 74.3 | 7.171 | 49.5
L4 | B2 | B25 | L4 | Line | 345 | 57.6 | -312.08 | 75.98 | 321.19 | -97.2 | 3.208 | 164.1 | 7.28 | -5.91 | 4.78 | 67.1 | 7.171 | 44.7
L5 | B3 | B4 | L5 | Line | 345 | 142.8 | -385.5 | 346.65 | 518.43 | -74.4 | 5.472 | -166.8 | 3.98 | 46.97 | 4.78 | 114.5 | 7.171 | 76.3
L6 | B3 | B18 | L6 | Line | 345 | 89.1 | -0.64 | 5.07 | 5.12 | -12.5 | 0.054 | -126 | 0 | -19.12 | 4.78 | 1.1 | 7.171 | 0.8
L7 | B4 | B5 | L7 | Line | 345 | 85.8 | -653.92 | 190.27 | 681.04 | -96 | 7.763 | 173.5 | 4.84 | 67.35 | 10.756 | 72.2 | 11.951 | 65
L8 | B4 | B14 | L8 | Line | 345 | 86.5 | -235.56 | -74.59 | 247.09 | -95.3 | 2.817 | 139.7 | 0.63 | -0.69 | 4.78 | 58.9 | 7.171 | 39.3
L9 | B5 | B6 | L9 | Line | 345 | 17.4 | -694.65 | -164.11 | 713.77 | -97.3 | 8.297 | 150.4 | 1.38 | 14.64 | 10.756 | 77.1 | 11.951 | 69.4
DC Line Report
ID | Bus From | Bus To | DBase ID | DC Current | DC Power Losses | Commut. X (Rectifier) | Commut. X (Inverter) | Alpha | Gamma | Gamma Min | PF (Rectifier) | PF (Inverter) | DC Voltage (Rectifier) | DC Voltage (Inverter) | DC Power (Rectifier) | DC Power (Inverter) | AC Volt (Rectifier) | AC Volt (Inverter) | P to Converter (Rectifier) | Q to Converter (Rectifier) | P to Converter (Inverter) | Q to Converter (Inverter) | P from Network (Rectifier) | Q from Network (Rectifier) | P from Network (Inverter) | Q from Network (Inverter)
DC1 | B39_REC | B9_INV | DC1 | 1000 | 1 | 2.83 | 2.83 | 23.7 | 0 | 10 | 0.93 | 0.95 | 500 | 499 | 501 | 500 | 102 | 71.3 | 501 | 176 | -500 | 117 | 502 | 195 | -499 | 154
Transformer
TXFO ID | Bus From | Bus To | DBase ID | Type | Rated S [MVA] | kV Nominal Primary | kV Nominal Secondary | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | Iangle [deg] | P losses [MW] | Q losses [MVAR] | Capacity (Norm.) [MVA] | Loading [%] Capacity | Capacity (Emer.) [MVA] | Loading [%] Capacity | Tap Ratio % | Tap Pos [%] | Min | Max | Setpoint Min | Setpoint Max | Ctrld Bus/V [pu] | Ctrled BusID
Tap Pos [%]
T10 | B2 | B30 | T10 | Fixed-Tap Xmer | 1000 | 345 | 16.5 | -249.28 | -242.98 | 348.1 | -71.6 | 3.477 | 106.1 | 0.73 | 21.88 | 1100 | 31.6 | 1150 | 30.3 | 100 | 100
T01 | B12 | B11 | T01 | Fixed-Tap Xmer | 300 | 138 | 345 | -27.72 | -36.17 | 45.57 | -60.8 | 0.525 | 111.9 | 0.04 | 1.2 | 500 | 9.1 | 550 | 8.3 | 100 | 100
T11 | B29 | B38 | T11 | Fixed-Tap Xmer | 1000 | 345 | 16.5 | -824.7 | 6.25 | 824.72 | -100 | 8.141 | 159.6 | 5.3 | 103.39 | 1100 | 75 | 1150 | 71.7 | 100 | 100
T02 | B12 | B13 | T02 | Fixed-Tap Xmer | 300 | 138 | 345 | 20.22 | -51.83 | 55.64 | 36.3 | 0.64 | 53.1 | 0.07 | 1.78 | 500 | 11.1 | 550 | 10.1 | 100 | 100
T12 | B19 | B20 | T12 | Fixed-Tap Xmer | 1000 | 345 | 230 | -377.05 | 16.92 | 377.43 | -99.9 | 3.916 | 168.6 | 1.07 | 21.17 | 1100 | 34.3 | 1150 | 32.8 | 100 | 100
T03 | B6 | B31 | T03 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -883.26 | -261.49 | 921.16 | -95.9 | 10.624 | 148.6 | 7.26 | 282.1 | 800 | 115.1 | 850 | 108.4 | 100 | 100
T04 | B10 | B32 | T04 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -646.82 | -312.26 | 718.24 | -90.1 | 7.982 | 139.7 | 3.18 | 127.39 | 900 | 79.8 | 950 | 75.6 | 100 | 100
T05 | B19 | B33 | T05 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -628.81 | -167.46 | 650.73 | -96.6 | 6.752 | 151.1 | 3.19 | 64.71 | 900 | 72.3 | 950 | 68.5 | 100 | 100
T06 | B20 | B34 | T06 | Fixed-Tap Xmer | 600 | 230 | 16.5 | -1006.12 | -107.24 | 1011.82 | -99.4 | 10.478 | 163.2 | 9.88 | 197.57 | 1400 | 72.3 | 1500 | 67.5 | 100 | 100
T07 | B22 | B35 | T07 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -647.03 | -473.02 | 801.49 | -80.7 | 8.24 | 118.1 | 2.97 | 97.14 | 900 | 89.1 | 950 | 84.4 | 100 | 100
T08 | B23 | B36 | T08 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -557.44 | -375.95 | 672.37 | -82.9 | 7.155 | 117.7 | 2.56 | 139.21 | 800 | 84 | 850 | 79.1 | 100 | 100
T09 | B25 | B37 | T09 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -538.32 | -3.94 | 538.33 | -100 | 5.297 | 151.8 | 1.68 | 65.1 | 800 | 67.3 | 850 | 63.3 | 100 | 100
[21 empty] | Tap Pos [%] | Min Tap [%] | Max Tap [%] | Bus Min V [pu] | Bus Max V [pu]
T_REC | B39 | B39_REC | T_REC | Tcul Xmer | 800 | 345 | 100 | 501.52 | 195.18 | 538.16 | 93.2 | 5.225 | -63.2 | 0.52 | 19.31 | 1100 | 48.9 | 1200 | 44.8 | 100 | 100 | 90 | 110 | 3.45 | 3.45 | 3.45 | B39_REC
T_INV | B9 | B9_INV | T_INV | Tcul Xmer | 800 | 345 | 100 | -499.02 | 154.08 | 522.27 | -95.5 | 7.2 | -161.2 | 0.98 | 36.67 | 1100 | 47.5 | 1200 | 43.5 | 100 | 100 | 90 | 110 | 3.45 | 3.45 | 3.45 | B9_INV
Abnormal Report
ID
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
B10 | 0 | 345 | 0.9 | 1.1 | 0.9 | -14.6
B11 | 0 | 345 | 0.9 | 1.1 | 0.888 | -14.7
B12 | 0 | 138 | 0.9 | 1.1 | 0.869 | -15.6
B13 | 0 | 345 | 0.9 | 1.1 | 0.894 | -16.3
B14 | 0 | 345 | 0.9 | 1.1 | 0.89 | -20.6
B9_INV | 0 | 100 | 0.9 | 1.1 | 0.713 | 5.6
B4 | 0 | 345 | 0.9 | 1.1 | 0.877 | -22.8
B5 | 0 | 345 | 0.9 | 1.1 | 0.86 | -16.3
B6 | 0 | 345 | 0.9 | 1.1 | 0.867 | -14.9
B7 | 0 | 345 | 0.9 | 1.1 | 0.833 | -16.5
B8 | 0 | 345 | 0.9 | 1.1 | 0.822 | -16.4
B9 | 0 | 345 | 0.9 | 1.1 | 0.725 | 1.6
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
L5 | B3 | B4 | 5.472 | 4.78 | 7.171
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L20 | B15 | B16 | 2.909 | 5.378
L30 | B25 | B26 | 0.383 | 2.39
L21 | B16 | B17 | 3.106 | 5.378
L12 | B6 | B11 | 2.571 | 5.378
L32 | B26 | B28 | 1.491 | 2.39
L13 | B7 | B8 | 2.478 | 5.378
L23 | B16 | B21 | 1.335 | 2.39
L33 | B26 | B29 | 1.969 | 2.39
L25 | B17 | B18 | 1.678 | 2.39
L16 | B10 | B11 | 2.877 | 5.378
L26 | B17 | B27 | 1.719 | 2.39
L27 | B21 | B22 | 2.725 | 3.986
L29 | B23 | B24 | 0.363 | 2.39
L6 | B3 | B18 | 0.054 | 2.39
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
T03 | B6 | B31 | 921.156 | 800 | 850
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B2 | B30 | 348.105 | 550
T01 | B12 | B11 | 45.569 | 250
T02 | B12 | B13 | 55.638 | 250
T12 | B19 | B20 | 377.429 | 550
T_REC | B39 | B39_REC | 538.163 | 550
T_INV | B9 | B9_INV | 522.269 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
G05 | B34 | 1016 | 304.82 | -2 | 2
G06 | B35 | 650 | 570.16 | -192 | 448
G07 | B36 | 560 | 515.17 | -168 | 392
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]
Summary Report
LOAD FLOW STUDY PARAMETERS
Study : |  |  | UNTITLED
Time : |  |  | Fri Jul 23 12h08m22s 2021
Method : |  |  | Newton-Raphson
Constraints : |  |  | Not applied
Flat start : |  |  | Yes
Tcul txfo used as fixed tap : |  |  | Yes
Block Q-flow Txfo Adjustment |  |  | n\a
Block P-flow Txfo Adjustment : |  |  | n\a
Block Switchable Shunt Adjustment : |  |  | n\a
Block DC Link Adjustment : |  |  | No
Base power : |  |  | 100.00 [MVA]
Tolerance : |  |  | 0.100 [MVA]
COMPLETE SUMMARY REPORT
Summary Data |  |  |  |  | Active Power |  | Reactive Power
Total generation |  |  |  |  | 7027.718 |  | 3658.901
Spinning reserve |  |  |  |  | 8362.282
Static Load |  |  |  |  | 6097.1 |  | 1408.9
Shunt loads |  |  |  |  | 0 |  | 0
Motor loads |  |  |  |  | 800 |  | 600
Total load |  |  |  |  | 6897.1 |  | 2008.9
Line / cable losses |  |  |  |  | 90.184 |  | 178.089
Transformer losses |  |  |  |  | 39.429 |  | 1178.627
Total losses |  |  |  |  | 130.614 |  | 1649.716
Mismatches |  |  |  |  | 0.004 |  | 0.285

## Static_VAR_Compensator
Bus
ID | Zone | kV Base | V sol [pu] | Ang sol [deg] | Vmin [pu] | Vmax [pu] | P Gen [MW] | Q Gen [MVAR] | P Load [MW] | Q Load [MVAR] | P motor [MW] | Q motor [MVAR] | P shunt [MW] | Q shunt [MVAR]
B1 | 0 | 345 | 1.015 | -2.3 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B10 | 0 | 345 | 0.983 | 0.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B11 | 0 | 345 | 0.986 | -0.1 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B12 | 0 | 138 | 0.963 | -0.1 | 0.9 | 1.1 | 0 | 0 | 7.5 | 88 | 0 | 0 | 0 | 0
B13 | 0 | 345 | 0.979 | 0 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B14 | 0 | 345 | 0.975 | -1.7 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B15 | 0 | 345 | 0.955 | -2.4 | 0.9 | 1.1 | 0 | 0 | 320 | 153 | 0 | 0 | 0 | 0
B16 | 0 | 345 | 0.962 | -0.9 | 0.9 | 1.1 | 0 | 0 | 329 | 32.3 | 0 | 0 | 0 | 0
B17 | 0 | 345 | 0.975 | -1.5 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B18 | 0 | 345 | 0.98 | -2.5 | 0.9 | 1.1 | 0 | 0 | 158 | 30 | 0 | 0 | 0 | 0
B19 | 0 | 345 | 0.97 | 13 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B2 | 0 | 345 | 1.017 | -0.1 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B20 | 0 | 230 | 0.969 | 16.2 | 0.9 | 1.1 | 0 | 0 | 628 | 103 | 0 | 0 | 0 | 0
B21 | 0 | 345 | 0.964 | -1.6 | 0.9 | 1.1 | 0 | 0 | 274 | 115 | 0 | 0 | 0 | 0
B22 | 0 | 345 | 0.983 | -0.1 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B23 | 0 | 345 | 0.951 | -2.7 | 0.9 | 1.1 | 0 | 0 | 247.5 | 84.6 | 800 | 600 | 0 | 0
B24 | 0 | 345 | 0.965 | -2.1 | 0.9 | 1.1 | 0 | 0 | 308.6 | -92.2 | 0 | 0 | 0 | 0
B25 | 0 | 345 | 1.031 | 2.6 | 0.9 | 1.1 | 0 | 0 | 224 | 47.2 | 0 | 0 | 0 | 0
B26 | 0 | 345 | 1.005 | 2.6 | 0.9 | 1.1 | 0 | 0 | 139 | 17 | 0 | 0 | 0 | 0
B27 | 0 | 345 | 0.984 | -0.5 | 0.9 | 1.1 | 0 | 0 | 281 | 75.5 | 0 | 0 | 0 | 0
B28 | 0 | 345 | 1.007 | 9 | 0.9 | 1.1 | 0 | 0 | 206 | 27.6 | 0 | 0 | 0 | 0
B29 | 0 | 345 | 1.011 | 12.7 | 0.9 | 1.1 | 0 | 0 | 283.5 | 26.9 | 0 | 0 | 0 | 0
B3 | 0 | 345 | 0.992 | -2.9 | 0.9 | 1.1 | 0 | 0 | 322 | 2.4 | 0 | 0 | 0 | 0
B30 | 0 | 16.5 | 1.048 | 2.9 | 0.9 | 1.1 | 307.53 | 176.83 | 0 | 0 | 0 | 0 | 0 | 0
B31 | 0 | 16.5 | 0.982 | 0 | 0.9 | 1.1 | 130.62 | -52.97 | 9.2 | 4.6 | 0 | 0 | 0 | 0
B32 | 0 | 16.5 | 0.983 | 8.5 | 0.9 | 1.1 | 650 | 30.12 | 0 | 0 | 0 | 0 | 0 | 0
B33 | 0 | 16.5 | 0.997 | 19.4 | 0.9 | 1.1 | 777.45 | 196.56 | 0 | 0 | 0 | 0 | 0 | 0
B34 | 0 | 16.5 | 1.012 | 26.7 | 0.9 | 1.1 | 1016 | 284.52 | 0 | 0 | 0 | 0 | 0 | 0
B35 | 0 | 16.5 | 1.049 | 5 | 0.9 | 1.1 | 650 | 496.5 | 0 | 0 | 0 | 0 | 0 | 0
B36 | 0 | 16.5 | 1.064 | 5.8 | 0.9 | 1.1 | 560 | 472.44 | 0 | 0 | 0 | 0 | 0 | 0
B37 | 0 | 16.5 | 1.028 | 11 | 0.9 | 1.1 | 664.27 | 19.23 | 0 | 0 | 0 | 0 | 0 | 0
B38 | 0 | 16.5 | 1.026 | 21.5 | 0.9 | 1.1 | 1021.01 | 126.75 | 0 | 0 | 0 | 0 | 0 | 0
B39 | 0 | 345 | 1.03 | -7.5 | 0.9 | 1.1 | 1230.13 | 498.58 | 1104 | 250 | 0 | 0 | 0 | 0
B39_REC | 0 | 100 | 1.016 | -9.5 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B4 | 0 | 345 | 0.978 | -3.6 | 0.9 | 1.1 | 0 | 0 | 500 | 184 | 0 | 0 | 0 | 0
B5 | 0 | 345 | 1 | -2.2 | 0.9 | 1.1 | 0 | 412.11 | 0 | 0 | 0 | 0 | 0 | 0
B6 | 0 | 345 | 0.996 | -1.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B7 | 0 | 345 | 1 | -2.8 | 0.9 | 1.1 | 0 | 406.12 | 233.8 | 84 | 0 | 0 | 0 | 0
B8 | 0 | 345 | 0.987 | -2.6 | 0.9 | 1.1 | 0 | 0 | 522 | 176 | 0 | 0 | 0 | 0
B9 | 0 | 345 | 0.932 | 8.9 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B9_INV | 0 | 100 | 0.923 | 11.3 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generator
ID | Bus ID | DBase ID | Type | Rated S [MVA] | kV Nominal | Generator Type | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | Q max. [MVAR] | Q min. [MVAR] | Ctrled BusID | Ctrld Bus/V [pu]
G10 | B30 | G10 | Generator | 1000 | 16.5 | PV | 307.53 | 176.83 | 354.75 | 86.7 | 3.387 | 560 | -240 | B30 | 1.048
G01 | B39 | G01 | Generator | 10000 | 345 | PV | 1230.13 | 498.58 | 1327.33 | 92.7 | 12.887 | 5600 | -2400 | B39 | 1.03
G02 | B31 | G02 | Generator | 700 | 16.5 | SW | 130.62 | -52.97 | 140.95 | 92.7 | 1.435 | 392 | -168 | B31 | 0.982
G03 | B32 | G03 | Generator | 800 | 16.5 | PV | 650 | 30.12 | 650.7 | 99.9 | 6.619 | 448 | -192 | B32 | 0.983
G04 | B33 | G04 | Generator | 800 | 16.5 | PV | 777.45 | 196.56 | 801.91 | 96.9 | 8.041 | 448 | -192 | B33 | 0.997
G05 | B34 | G05 | Generator | 600 | 16.5 | PV | 1016 | 1.68 | 1016 | 100 | 10.037 | 2 | -2 | B34 | 1.012
G06 | B35 | G06 | Generator | 800 | 16.5 | PV | 650 | 266.34 | 702.45 | 92.5 | 6.695 | 448 | -192 | B35 | 1.049
G07 | B36 | G07 | Generator | 700 | 16.5 | PV | 560 | 248.45 | 612.64 | 91.4 | 5.761 | 392 | -168 | B36 | 1.064
G08 | B37 | G08 | Generator | 700 | 16.5 | PV | 664.27 | 19.23 | 664.55 | 100 | 6.466 | 392 | -168 | B37 | 1.028
G09 | B38 | G09 | Generator | 1000 | 16.5 | PV | 1021.01 | 126.75 | 1028.85 | 99.2 | 10.023 | 560 | -240 | B38 | 1.026
SVC1 | B34 | SVC1 | Static Var Compensator | 335 | 16.5 | PV | 0 | 282.85 | 282.85 | 0 | 2.794 | 335 | -310 | B34 | 1.012
SVC2 | B35 | SVC2 | Static Var Compensator | 368.91 | 16.5 | PV | 0 | 230.16 | 230.16 | 0 | 2.194 | 368.91 | -119.91 | B35 | 1.049
SVC3 | B36 | SVC3 | Static Var Compensator | 341.8 | 16.5 | PV | 0 | 223.99 | 223.99 | 0 | 2.106 | 341.8 | -117.8 | B36 | 1.064
SVC4 | B5 | SVC4 | Static Var Compensator | 450 | 345 | PV | 0 | 412.11 | 412.11 | 0 | 4.121 | 450 | -180 | B5 | 1
SVC5 | B7 | SVC5 | Static Var Compensator | 450 | 345 | PV | 0 | 406.12 | 406.12 | 0 | 4.061 | 450 | -200 | B7 | 1
Distributed Swing Report
ID | P Desired [MW] | P calculated [MW]
G10 | 250 | 307.53
G04 | 632 | 777.45
G08 | 540 | 664.27
G09 | 830 | 1021.01
G01 | 1000 | 1230.13
Motor
ID | Bus ID | DBase ID | Type | V sol [pu] | S [MVA] | P. Factor [%] | I [pu]
IM1 | B23 | IM1 | Induction Motor | 0.951 | 1000 | 80 | 10.52
Static Load
ID | Bus ID | DBase ID | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%]
S10 | B21 | S10 | 274 | 115 | 297.15 | 92.2
S01 | B3 | S01 | 322 | 2.4 | 322.01 | 100
S11 | B23 | S11 | 247.5 | 84.6 | 261.56 | 94.6
S02 | B4 | S02 | 500 | 184 | 532.78 | 93.8
S12 | B24 | S12 | 308.6 | -92.2 | 322.08 | 95.8
S03 | B7 | S03 | 233.8 | 84 | 248.43 | 94.1
S13 | B25 | S13 | 224 | 47.2 | 228.92 | 97.9
S04 | B8 | S04 | 522 | 176 | 550.87 | 94.8
S14 | B26 | S14 | 139 | 17 | 140.04 | 99.3
S05 | B12 | S05 | 7.5 | 88 | 88.32 | 8.5
S15 | B27 | S15 | 281 | 75.5 | 290.97 | 96.6
S06 | B15 | S06 | 320 | 153 | 354.7 | 90.2
S16 | B28 | S16 | 206 | 27.6 | 207.84 | 99.1
S07 | B16 | S07 | 329 | 32.3 | 330.58 | 99.5
S17 | B29 | S17 | 283.5 | 26.9 | 284.77 | 99.6
S08 | B18 | S08 | 158 | 30 | 160.82 | 98.2
S18 | B31 | S18 | 9.2 | 4.6 | 10.29 | 89.4
S09 | B20 | S09 | 628 | 103 | 636.39 | 98.7
S19 | B39 | S19 | 1104 | 250 | 1131.95 | 97.5
Branch
ID | Bus From | Bus To | DBase ID | Type | kV Nominal | Length | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | I angle [deg] | P losses [MW] | Q losses [MVAR] | Ampacity (Norm.) [pu] | Loading % | Ampacity (Emer.) [pu] | Loading(Emer) %
L10 | B5 | B8 | L10 | Line | 345 | 75.1 | 72.96 | 100.13 | 123.9 | 58.9 | 1.239 | -56.1 | 0.13 | -12.68 | 4.78 | 25.9 | 7.171 | 17.3
L20 | B15 | B16 | L20 | Line | 345 | 63 | -265.33 | -53.21 | 270.61 | -98 | 2.835 | 166.3 | 0.72 | -8.23 | 10.756 | 26.4 | 11.951 | 23.7
L30 | B25 | B26 | L30 | Line | 345 | 216.5 | 6.12 | 52.69 | 53.04 | 11.5 | 0.515 | -80.8 | 0.19 | -51.21 | 4.78 | 10.8 | 7.171 | 7.2
L11 | B6 | B7 | L11 | Line | 345 | 61.7 | 191.14 | -55.93 | 199.15 | 96 | 1.999 | 14.5 | 0.24 | -7.64 | 4.78 | 41.8 | 7.171 | 27.9
L21 | B16 | B17 | L21 | Line | 345 | 59.7 | 104.4 | -152.21 | 184.57 | 56.6 | 1.919 | 54.7 | 0.24 | -9.49 | 10.756 | 17.8 | 11.951 | 16.1
L31 | B26 | B27 | L31 | Line | 345 | 98.5 | 380.8 | 106.52 | 395.42 | 96.3 | 3.933 | -13 | 2.2 | -0.58 | 4.78 | 82.3 | 7.171 | 54.9
L12 | B6 | B11 | L12 | Line | 345 | 55 | -341.55 | 155.72 | 375.37 | -91 | 3.767 | -157.3 | 1.01 | -1.82 | 10.756 | 35 | 11.951 | 31.5
L22 | B16 | B19 | L22 | Line | 345 | 130.7 | -1127.42 | 177.51 | 1141.31 | -98.8 | 11.865 | -171.9 | 22.66 | 247.28 | 11.951 | 99.3 | 12.549 | 94.6
L32 | B26 | B28 | L32 | Line | 345 | 317.7 | -232.61 | -9.16 | 232.79 | -99.9 | 2.316 | -179.6 | 2.34 | -53.2 | 4.78 | 48.4 | 7.171 | 32.3
L13 | B7 | B8 | L13 | Line | 345 | 30.8 | -42.9 | 273.83 | 277.17 | -15.5 | 2.772 | -101.7 | 0.32 | -4.07 | 10.756 | 25.8 | 11.951 | 23.2
L23 | B16 | B21 | L23 | Line | 345 | 90.5 | 89.03 | -33.27 | 95.04 | 93.7 | 0.988 | 19.6 | 0.07 | -22.41 | 4.78 | 20.7 | 7.171 | 13.8
L33 | B26 | B29 | L33 | Line | 345 | 418.9 | -281.26 | -10.46 | 281.46 | -99.9 | 2.8 | -179.5 | 4.56 | -54.6 | 4.78 | 58.6 | 7.171 | 39
L14 | B8 | B9 | L14 | Line | 345 | 243.3 | -492.39 | 214.72 | 537.17 | -91.7 | 5.44 | -159.1 | 7.03 | 75.42 | 10.756 | 50.6 | 11.951 | 45.5
L24 | B16 | B24 | L24 | Line | 345 | 39.5 | 338.94 | -69.32 | 345.96 | 98 | 3.597 | 10.7 | 0.38 | 1.29 | 4.78 | 75.2 | 7.171 | 50.2
L34 | B28 | B29 | L34 | Line | 345 | 101.2 | -440.95 | 16.44 | 441.26 | -99.9 | 4.381 | -168.9 | 2.7 | 3.72 | 4.78 | 91.7 | 7.171 | 61.1
L25 | B17 | B18 | L25 | Line | 345 | 55 | 201.6 | -82.37 | 217.78 | 92.6 | 2.234 | 20.7 | 0.34 | -8.59 | 4.78 | 46.7 | 7.171 | 31.2
L16 | B10 | B11 | L16 | Line | 345 | 28.8 | 344.57 | -106.17 | 360.56 | 95.6 | 3.67 | 17.9 | 0.53 | -1.3 | 10.756 | 34.1 | 11.951 | 30.7
L26 | B17 | B27 | L26 | Line | 345 | 116 | -97.44 | -60.35 | 114.62 | -85 | 1.176 | 146.7 | 0.16 | -28.75 | 4.78 | 24.6 | 7.171 | 16.4
L17 | B10 | B13 | L17 | Line | 345 | 28.8 | 303.24 | 48.7 | 307.12 | 98.7 | 3.126 | -8.3 | 0.39 | -2.8 | 10.756 | 29.1 | 11.951 | 26.2
L27 | B21 | B22 | L27 | Line | 345 | 93.8 | -185.04 | -125.86 | 223.79 | -82.7 | 2.321 | 144.2 | 0.41 | -17.2 | 7.971 | 29.1 | 11.951 | 19.4
L18 | B13 | B14 | L18 | Line | 345 | 67.7 | 296.76 | 14.28 | 297.1 | 99.9 | 3.034 | -2.7 | 0.83 | -7.11 | 10.756 | 28.2 | 11.951 | 25.4
L28 | B22 | B23 | L28 | Line | 345 | 64.3 | 461.89 | 300.91 | 551.26 | 83.8 | 5.61 | -33.2 | 1.92 | 13.5 | 7.171 | 78.2 | 9.561 | 58.7
L19 | B14 | B15 | L19 | Line | 345 | 145.4 | 54.86 | 68.09 | 87.44 | 62.7 | 0.897 | -52.9 | 0.2 | -31.7 | 4.78 | 18.8 | 7.171 | 12.5
L29 | B23 | B24 | L29 | Line | 345 | 234.6 | -29.9 | -53.82 | 61.57 | -48.6 | 0.648 | 116.4 | 0.06 | -32.23 | 4.78 | 13.5 | 7.171 | 9
L1 | B1 | B2 | L1 | Line | 345 | 275.5 | -376.8 | 96.59 | 388.98 | -96.9 | 3.832 | -168 | 5.41 | -57.38 | 10.756 | 35.6 | 11.951 | 32.1
L2 | B1 | B39 | L2 | Line | 345 | 167.6 | 376.8 | -96.59 | 388.98 | 96.9 | 3.832 | 12 | 1.41 | -43.19 | 10.756 | 35.6 | 11.951 | 32.1
L3 | B2 | B3 | L3 | Line | 345 | 101.2 | 342.1 | 130.23 | 366.05 | 93.5 | 3.601 | -20.9 | 1.73 | -5.84 | 4.78 | 75.3 | 7.171 | 50.2
L4 | B2 | B25 | L4 | Line | 345 | 57.6 | -417.47 | 179.81 | 454.54 | -91.8 | 4.471 | -156.8 | 14.18 | 2.13 | 4.78 | 93.5 | 7.171 | 62.4
L5 | B3 | B4 | L5 | Line | 345 | 142.8 | 61.5 | 49.2 | 78.76 | 78.1 | 0.794 | -41.6 | 0.1 | -19.89 | 4.78 | 16.6 | 7.171 | 11.1
L6 | B3 | B18 | L6 | Line | 345 | 89.1 | -43.13 | 84.47 | 94.85 | -45.5 | 0.956 | -120 | 0.12 | -19.31 | 4.78 | 20 | 7.171 | 13.3
L7 | B4 | B5 | L7 | Line | 345 | 85.8 | -198.03 | -156.53 | 252.43 | -78.5 | 2.58 | 138 | 0.52 | -4.88 | 10.756 | 24 | 11.951 | 21.6
L8 | B4 | B14 | L8 | Line | 345 | 86.5 | -240.56 | 41.63 | 244.14 | -98.5 | 2.495 | -173.8 | 0.5 | -5.07 | 4.78 | 52.2 | 7.171 | 34.8
L9 | B5 | B6 | L9 | Line | 345 | 17.4 | -271.51 | 160.32 | 315.31 | -86.1 | 3.153 | -151.7 | 0.2 | -1.72 | 10.756 | 29.3 | 11.951 | 26.4
DC Line Report
ID | Bus From | Bus To | DBase ID | DC Current | DC Power Losses | Commut. X (Rectifier) | Commut. X (Inverter) | Alpha | Gamma | Gamma Min | PF (Rectifier) | PF (Inverter) | DC Voltage (Rectifier) | DC Voltage (Inverter) | DC Power (Rectifier) | DC Power (Inverter) | AC Volt (Rectifier) | AC Volt (Inverter) | P to Converter (Rectifier) | Q to Converter (Rectifier) | P to Converter (Inverter) | Q to Converter (Inverter) | P from Network (Rectifier) | Q from Network (Rectifier) | P from Network (Inverter) | Q from Network (Inverter)
DC1 | B39_REC | B9_INV | DC1 | 1000 | 1 | 2.83 | 2.83 | 23.7 | 0 | 10 | 0.93 | 0.96 | 500 | 499 | 501 | 500 | 102 | 92.3 | 501 | 176 | -500 | 117 | 502 | 195 | -499 | 139
Transformer
TXFO ID | Bus From | Bus To | DBase ID | Type | Rated S [MVA] | kV Nominal Primary | kV Nominal Secondary | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | Iangle [deg] | P losses [MW] | Q losses [MVAR] | Capacity (Norm.) [MVA] | Loading [%] Capacity | Capacity (Emer.) [MVA] | Loading [%] Capacity | Tap Ratio % | Tap Pos [%] | Min | Max | Setpoint Min | Setpoint Max | Ctrld Bus/V [pu] | Ctrled BusID
Tap Pos [%]
T10 | B2 | B30 | T10 | Fixed-Tap Xmer | 1000 | 345 | 16.5 | -306.85 | -156.07 | 344.26 | -89.1 | 3.387 | 153 | 0.69 | 20.76 | 1100 | 31.3 | 1150 | 29.9 | 100 | 100
T01 | B12 | B11 | T01 | Fixed-Tap Xmer | 300 | 138 | 345 | -1.44 | -51.44 | 51.46 | -2.8 | 0.535 | 91.5 | 0.05 | 1.24 | 500 | 10.3 | 550 | 9.4 | 100 | 100
T11 | B29 | B38 | T11 | Fixed-Tap Xmer | 1000 | 345 | 16.5 | -1012.98 | 29.96 | 1013.42 | -100 | 10.023 | -165.6 | 8.04 | 156.71 | 1100 | 92.1 | 1150 | 88.1 | 100 | 100
T02 | B12 | B13 | T02 | Fixed-Tap Xmer | 300 | 138 | 345 | -6.06 | -36.56 | 37.06 | -16.4 | 0.385 | 99.3 | 0.02 | 0.65 | 500 | 7.4 | 550 | 6.7 | 100 | 100
T12 | B19 | B20 | T12 | Fixed-Tap Xmer | 1000 | 345 | 230 | -377.16 | 35 | 378.78 | -99.6 | 3.905 | -161.7 | 1.07 | 21.05 | 1100 | 34.4 | 1150 | 32.9 | 100 | 100
T03 | B6 | B31 | T03 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -121.3 | 62.25 | 136.34 | -89 | 1.368 | -154.6 | 0.12 | 4.68 | 800 | 17 | 850 | 16 | 100 | 100
T04 | B10 | B32 | T04 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -647.81 | 57.47 | 650.35 | -99.6 | 6.619 | -174.1 | 2.19 | 87.59 | 900 | 72.3 | 950 | 68.5 | 100 | 100
T05 | B19 | B33 | T05 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -772.92 | -104.76 | 779.99 | -99.1 | 8.041 | -174.8 | 4.53 | 91.79 | 900 | 86.7 | 950 | 82.1 | 100 | 100
T06 | B20 | B34 | T06 | Fixed-Tap Xmer | 600 | 230 | 16.5 | -1006.23 | -89.05 | 1010.16 | -99.6 | 10.423 | -168.9 | 9.77 | 195.47 | 1400 | 72.2 | 1500 | 67.3 | 100 | 100
T07 | B22 | B35 | T07 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -647.34 | -409.57 | 766.02 | -84.5 | 7.795 | 147.6 | 2.66 | 86.93 | 900 | 85.1 | 950 | 80.6 | 100 | 100
T08 | B23 | B36 | T08 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -557.63 | -343.37 | 654.87 | -85.2 | 6.889 | 145.7 | 2.37 | 129.07 | 800 | 81.9 | 850 | 77 | 100 | 100
T09 | B25 | B37 | T09 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -661.77 | 77.79 | 666.32 | -99.3 | 6.466 | -170.7 | 2.51 | 97.01 | 800 | 83.3 | 850 | 78.4 | 100 | 100
[21 empty] | Tap Pos [%] | Min Tap [%] | Max Tap [%] | Bus Min V [pu] | Bus Max V [pu]
T_REC | B39 | B39_REC | T_REC | Tcul Xmer | 800 | 345 | 100 | 501.52 | 195.18 | 538.16 | 93.2 | 5.225 | -28.8 | 0.52 | 19.31 | 1100 | 48.9 | 1200 | 44.8 | 100 | 100 | 90 | 110 | 3.45 | 3.45 | 3.45 | B39_REC
T_INV | B9 | B9_INV | T_INV | Tcul Xmer | 800 | 345 | 100 | -499.42 | 139.3 | 518.48 | -96.3 | 5.563 | -155.5 | 0.58 | 21.89 | 1100 | 47.1 | 1200 | 43.2 | 100 | 100 | 90 | 110 | 3.45 | 3.45 | 3.45 | B9_INV
Abnormal Report
ID
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L10 | B5 | B8 | 1.239 | 2.39
L20 | B15 | B16 | 2.835 | 5.378
L30 | B25 | B26 | 0.515 | 2.39
L11 | B6 | B7 | 1.999 | 2.39
L21 | B16 | B17 | 1.919 | 5.378
L12 | B6 | B11 | 3.767 | 5.378
L32 | B26 | B28 | 2.316 | 2.39
L13 | B7 | B8 | 2.772 | 5.378
L23 | B16 | B21 | 0.988 | 2.39
L25 | B17 | B18 | 2.234 | 2.39
L16 | B10 | B11 | 3.67 | 5.378
L26 | B17 | B27 | 1.176 | 2.39
L17 | B10 | B13 | 3.126 | 5.378
L27 | B21 | B22 | 2.321 | 3.986
L18 | B13 | B14 | 3.034 | 5.378
L19 | B14 | B15 | 0.897 | 2.39
L29 | B23 | B24 | 0.648 | 2.39
L1 | B1 | B2 | 3.832 | 5.378
L2 | B1 | B39 | 3.832 | 5.378
L5 | B3 | B4 | 0.794 | 2.39
L6 | B3 | B18 | 0.956 | 2.39
L7 | B4 | B5 | 2.58 | 5.378
L9 | B5 | B6 | 3.153 | 5.378
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B2 | B30 | 344.256 | 550
T01 | B12 | B11 | 51.457 | 250
T02 | B12 | B13 | 37.062 | 250
T12 | B19 | B20 | 378.78 | 550
T03 | B6 | B31 | 136.341 | 400
T_REC | B39 | B39_REC | 538.163 | 550
T_INV | B9 | B9_INV | 518.482 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]
Summary Report
LOAD FLOW STUDY PARAMETERS
Study : |  |  | UNTITLED
Time : |  |  | Fri Jul 23 12h15m58s 2021
Method : |  |  | Newton-Raphson
Constraints : |  |  | Not applied
Flat start : |  |  | Yes
Tcul txfo used as fixed tap : |  |  | Yes
Block Q-flow Txfo Adjustment |  |  | n\a
Block P-flow Txfo Adjustment : |  |  | n\a
Block Switchable Shunt Adjustment : |  |  | n\a
Block DC Link Adjustment : |  |  | No
Base power : |  |  | 100.00 [MVA]
Tolerance : |  |  | 0.100 [MVA]
COMPLETE SUMMARY REPORT
Summary Data |  |  |  |  | Active Power |  | Reactive Power
Total generation |  |  |  |  | 7007.016 |  | 3066.789
Spinning reserve |  |  |  |  | 8382.984
Static Load |  |  |  |  | 6097.1 |  | 1408.9
Shunt loads |  |  |  |  | 0 |  | 0
Motor loads |  |  |  |  | 800 |  | 600
Total load |  |  |  |  | 6897.1 |  | 2008.9
Line / cable losses |  |  |  |  | 73.803 |  | -169.551
Transformer losses |  |  |  |  | 35.112 |  | 934.155
Total losses |  |  |  |  | 109.915 |  | 1057.604
Mismatches |  |  |  |  | 0 |  | 0.285

## Shunt_Capacitor
Bus
ID | Zone | kV Base | V sol [pu] | Ang sol [deg] | Vmin [pu] | Vmax [pu] | P Gen [MW] | Q Gen [MVAR] | P Load [MW] | Q Load [MVAR] | P motor [MW] | Q motor [MVAR] | P shunt [MW] | Q shunt [MVAR]
B1 | 0 | 345 | 1.016 | -2.3 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B10 | 0 | 345 | 0.989 | 0.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B11 | 0 | 345 | 0.994 | -0.1 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B12 | 0 | 138 | 0.97 | -0.1 | 0.9 | 1.1 | 0 | 0 | 7.5 | 88 | 0 | 0 | 0 | 0
B13 | 0 | 345 | 0.986 | 0 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B14 | 0 | 345 | 0.981 | -1.7 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B15 | 0 | 345 | 0.958 | -2.3 | 0.9 | 1.1 | 0 | 0 | 320 | 153 | 0 | 0 | 0 | 0
B16 | 0 | 345 | 0.964 | -0.8 | 0.9 | 1.1 | 0 | 0 | 329 | 32.3 | 0 | 0 | 0 | 0
B17 | 0 | 345 | 0.977 | -1.4 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B18 | 0 | 345 | 0.983 | -2.5 | 0.9 | 1.1 | 0 | 0 | 158 | 30 | 0 | 0 | 0 | 0
B19 | 0 | 345 | 0.971 | 13 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B2 | 0 | 345 | 1.018 | 0 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B20 | 0 | 230 | 0.97 | 16.2 | 0.9 | 1.1 | 0 | 0 | 628 | 103 | 0 | 0 | 0 | 0
B21 | 0 | 345 | 0.966 | -1.6 | 0.9 | 1.1 | 0 | 0 | 274 | 115 | 0 | 0 | 0 | 0
B22 | 0 | 345 | 0.984 | 0 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B23 | 0 | 345 | 0.952 | -2.6 | 0.9 | 1.1 | 0 | 0 | 247.5 | 84.6 | 800 | 600 | 0 | 0
B24 | 0 | 345 | 0.967 | -2.1 | 0.9 | 1.1 | 0 | 0 | 308.6 | -92.2 | 0 | 0 | 0 | 0
B25 | 0 | 345 | 1.032 | 2.6 | 0.9 | 1.1 | 0 | 0 | 224 | 47.2 | 0 | 0 | 0 | 0
B26 | 0 | 345 | 1.007 | 2.7 | 0.9 | 1.1 | 0 | 0 | 139 | 17 | 0 | 0 | 0 | 0
B27 | 0 | 345 | 0.986 | -0.5 | 0.9 | 1.1 | 0 | 0 | 281 | 75.5 | 0 | 0 | 0 | 0
B28 | 0 | 345 | 1.008 | 9 | 0.9 | 1.1 | 0 | 0 | 206 | 27.6 | 0 | 0 | 0 | 0
B29 | 0 | 345 | 1.012 | 12.8 | 0.9 | 1.1 | 0 | 0 | 283.5 | 26.9 | 0 | 0 | 0 | 0
B3 | 0 | 345 | 0.996 | -2.9 | 0.9 | 1.1 | 0 | 0 | 322 | 2.4 | 0 | 0 | 0 | 0
B30 | 0 | 16.5 | 1.048 | 2.9 | 0.9 | 1.1 | 307.51 | 168.41 | 0 | 0 | 0 | 0 | 0 | 0
B31 | 0 | 16.5 | 0.982 | 0 | 0.9 | 1.1 | 130.62 | -96.25 | 9.2 | 4.6 | 0 | 0 | 0 | 0
B32 | 0 | 16.5 | 0.983 | 8.5 | 0.9 | 1.1 | 650 | -3.53 | 0 | 0 | 0 | 0 | 0 | 0
B33 | 0 | 16.5 | 0.997 | 19.4 | 0.9 | 1.1 | 777.38 | 190.47 | 0 | 0 | 0 | 0 | 0 | 0
B34 | 0 | 16.5 | 1.012 | 26.7 | 0.9 | 1.1 | 1016 | -0.13 | 0 | 0 | 0 | 0 | 0 | -275
B35 | 0 | 16.5 | 1.049 | 5 | 0.9 | 1.1 | 650 | 82.25 | 0 | 0 | 0 | 0 | 0 | -370
B36 | 0 | 16.5 | 1.064 | 5.9 | 0.9 | 1.1 | 560 | 78.23 | 0 | 0 | 0 | 0 | 0 | -345
B37 | 0 | 16.5 | 1.028 | 11 | 0.9 | 1.1 | 664.22 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0
B38 | 0 | 16.5 | 1.026 | 21.5 | 0.9 | 1.1 | 1020.93 | 123.33 | 0 | 0 | 0 | 0 | 0 | 0
B39 | 0 | 345 | 1.03 | -7.5 | 0.9 | 1.1 | 1230.04 | 494.13 | 1104 | 250 | 0 | 0 | 0 | 0
B39_REC | 0 | 100 | 1.016 | -9.4 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B4 | 0 | 345 | 0.987 | -3.6 | 0.9 | 1.1 | 0 | 0 | 500 | 184 | 0 | 0 | 0 | 0
B5 | 0 | 345 | 1.012 | -2.2 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -450
B6 | 0 | 345 | 1.007 | -1.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B7 | 0 | 345 | 1.015 | -2.8 | 0.9 | 1.1 | 0 | 0 | 233.8 | 84 | 0 | 0 | 0 | -450
B8 | 0 | 345 | 1.002 | -2.6 | 0.9 | 1.1 | 0 | 0 | 522 | 176 | 0 | 0 | 0 | 0
B9 | 0 | 345 | 0.949 | 8.5 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B9_INV | 0 | 100 | 0.94 | 10.8 | 0.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generator
ID | Bus ID | DBase ID | Type | Rated S [MVA] | kV Nominal | Generator Type | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | Q max. [MVAR] | Q min. [MVAR] | Ctrled BusID | Ctrld Bus/V [pu]
G10 | B30 | G10 | Generator | 1000 | 16.5 | PV | 307.51 | 168.41 | 350.6 | 87.7 | 3.347 | 560 | -240 | B30 | 1.048
G01 | B39 | G01 | Generator | 10000 | 345 | PV | 1230.04 | 494.13 | 1325.58 | 92.8 | 12.87 | 5600 | -2400 | B39 | 1.03
G02 | B31 | G02 | Generator | 700 | 16.5 | SW | 130.62 | -96.25 | 162.25 | 80.5 | 1.652 | 392 | -168 | B31 | 0.982
G03 | B32 | G03 | Generator | 800 | 16.5 | PV | 650 | -3.53 | 650.01 | 100 | 6.612 | 448 | -192 | B32 | 0.983
G04 | B33 | G04 | Generator | 800 | 16.5 | PV | 777.38 | 190.47 | 800.38 | 97.1 | 8.026 | 448 | -192 | B33 | 0.997
G05 | B34 | G05 | Generator | 600 | 16.5 | PV | 1016 | -0.13 | 1016 | 100 | 10.037 | 2 | -2 | B34 | 1.012
G06 | B35 | G06 | Generator | 800 | 16.5 | PV | 650 | 82.25 | 655.18 | 99.2 | 6.244 | 448 | -192 | B35 | 1.049
G07 | B36 | G07 | Generator | 700 | 16.5 | PV | 560 | 78.23 | 565.44 | 99 | 5.317 | 392 | -168 | B36 | 1.064
G08 | B37 | G08 | Generator | 700 | 16.5 | PV | 664.22 | 14.3 | 664.37 | 100 | 6.464 | 392 | -168 | B37 | 1.028
G09 | B38 | G09 | Generator | 1000 | 16.5 | PV | 1020.93 | 123.33 | 1028.35 | 99.3 | 10.018 | 560 | -240 | B38 | 1.026
Distributed Swing Report
ID | P Desired [MW] | P calculated [MW]
G10 | 250 | 307.51
G04 | 632 | 777.38
G08 | 540 | 664.22
G09 | 830 | 1020.93
G01 | 1000 | 1230.04
Motor
ID | Bus ID | DBase ID | Type | V sol [pu] | S [MVA] | P. Factor [%] | I [pu]
IM1 | B23 | IM1 | Induction Motor | 0.952 | 1000 | 80 | 10.509
Shunt
ID | Bus ID | DBase ID | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | R [MW] | X [MVAR] | Type
SC1 | B34 | ST1 | 0 | -281.81 | 281.81 | 0 | 0 | -275 | Shunt Capacitor
SC2 | B35 | ST2 | 0 | -407.36 | 407.36 | 0 | 0 | -370 | Shunt Capacitor
SC3 | B36 | ST3 | 0 | -390.22 | 390.22 | 0 | 0 | -345 | Shunt Capacitor
SC4 | B5 | ST4 | 0 | -460.82 | 460.82 | 0 | 0 | -450 | Shunt Capacitor
SC5 | B7 | ST5 | 0 | -463.49 | 463.49 | 0 | 0 | -450 | Shunt Capacitor
Static Load
ID | Bus ID | DBase ID | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%]
S10 | B21 | S10 | 274 | 115 | 297.15 | 92.2
S01 | B3 | S01 | 322 | 2.4 | 322.01 | 100
S11 | B23 | S11 | 247.5 | 84.6 | 261.56 | 94.6
S02 | B4 | S02 | 500 | 184 | 532.78 | 93.8
S12 | B24 | S12 | 308.6 | -92.2 | 322.08 | 95.8
S03 | B7 | S03 | 233.8 | 84 | 248.43 | 94.1
S13 | B25 | S13 | 224 | 47.2 | 228.92 | 97.9
S04 | B8 | S04 | 522 | 176 | 550.87 | 94.8
S14 | B26 | S14 | 139 | 17 | 140.04 | 99.3
S05 | B12 | S05 | 7.5 | 88 | 88.32 | 8.5
S15 | B27 | S15 | 281 | 75.5 | 290.97 | 96.6
S06 | B15 | S06 | 320 | 153 | 354.7 | 90.2
S16 | B28 | S16 | 206 | 27.6 | 207.84 | 99.1
S07 | B16 | S07 | 329 | 32.3 | 330.58 | 99.5
S17 | B29 | S17 | 283.5 | 26.9 | 284.77 | 99.6
S08 | B18 | S08 | 158 | 30 | 160.82 | 98.2
S18 | B31 | S18 | 9.2 | 4.6 | 10.29 | 89.4
S09 | B20 | S09 | 628 | 103 | 636.39 | 98.7
S19 | B39 | S19 | 1104 | 250 | 1131.95 | 97.5
Branch
ID | Bus From | Bus To | DBase ID | Type | kV Nominal | Length | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | I angle [deg] | P losses [MW] | Q losses [MVAR] | Ampacity (Norm.) [pu] | Loading % | Ampacity (Emer.) [pu] | Loading(Emer) %
L10 | B5 | B8 | L10 | Line | 345 | 75.1 | 72.6 | 79.12 | 107.38 | 67.6 | 1.061 | -49.7 | 0.1 | -13.57 | 4.78 | 22.2 | 7.171 | 14.8
L20 | B15 | B16 | L20 | Line | 345 | 63 | -265.57 | -39.93 | 268.56 | -98.9 | 2.802 | 169.1 | 0.7 | -8.48 | 10.756 | 26.1 | 11.951 | 23.4
L30 | B25 | B26 | L30 | Line | 345 | 216.5 | 6.38 | 51.51 | 51.91 | 12.3 | 0.503 | -80.3 | 0.19 | -51.4 | 4.78 | 10.5 | 7.171 | 7
L11 | B6 | B7 | L11 | Line | 345 | 61.7 | 191.25 | -98.8 | 215.26 | 88.8 | 2.137 | 25.5 | 0.27 | -7.45 | 4.78 | 44.7 | 7.171 | 29.8
L21 | B16 | B17 | L21 | Line | 345 | 59.7 | 104.26 | -154.54 | 186.42 | 55.9 | 1.933 | 55.2 | 0.25 | -9.51 | 10.756 | 18 | 11.951 | 16.2
L31 | B26 | B27 | L31 | Line | 345 | 98.5 | 381.01 | 102.82 | 394.64 | 96.5 | 3.92 | -12.4 | 2.19 | -0.83 | 4.78 | 82 | 7.171 | 54.7
L12 | B6 | B11 | L12 | Line | 345 | 55 | -341.95 | 191.33 | 391.84 | -87.3 | 3.89 | -152.6 | 1.07 | -1.28 | 10.756 | 36.2 | 11.951 | 32.5
L22 | B16 | B19 | L22 | Line | 345 | 130.7 | -1127.45 | 184.93 | 1142.52 | -98.7 | 11.847 | -171.5 | 22.6 | 246.4 | 11.951 | 99.1 | 12.549 | 94.4
L32 | B26 | B28 | L32 | Line | 345 | 317.7 | -232.56 | -7.79 | 232.7 | -99.9 | 2.311 | -179.2 | 2.34 | -53.41 | 4.78 | 48.3 | 7.171 | 32.2
L13 | B7 | B8 | L13 | Line | 345 | 30.8 | -42.81 | 288.15 | 291.31 | -14.7 | 2.87 | -101.3 | 0.34 | -4.04 | 10.756 | 26.7 | 11.951 | 24
L23 | B16 | B21 | L23 | Line | 345 | 90.5 | 88.91 | -28.16 | 93.26 | 95.3 | 0.967 | 16.8 | 0.07 | -22.55 | 4.78 | 20.2 | 7.171 | 13.5
L33 | B26 | B29 | L33 | Line | 345 | 418.9 | -281.25 | -9.12 | 281.4 | -99.9 | 2.795 | -179.2 | 4.55 | -54.88 | 4.78 | 58.5 | 7.171 | 39
L14 | B8 | B9 | L14 | Line | 345 | 243.3 | -492.66 | 208.87 | 535.11 | -92.1 | 5.341 | -159.7 | 6.78 | 70.34 | 10.756 | 49.7 | 11.951 | 44.7
L24 | B16 | B24 | L24 | Line | 345 | 39.5 | 339.01 | -65.98 | 345.37 | 98.2 | 3.581 | 10.2 | 0.38 | 1.2 | 4.78 | 74.9 | 7.171 | 49.9
L34 | B28 | B29 | L34 | Line | 345 | 101.2 | -440.9 | 18.02 | 441.27 | -99.9 | 4.378 | -168.7 | 2.7 | 3.65 | 4.78 | 91.6 | 7.171 | 61.1
L25 | B17 | B18 | L25 | Line | 345 | 55 | 201.69 | -87.92 | 220.02 | 91.7 | 2.251 | 22.1 | 0.35 | -8.61 | 4.78 | 47.1 | 7.171 | 31.4
L16 | B10 | B11 | L16 | Line | 345 | 28.8 | 344.97 | -139.39 | 372.06 | 92.7 | 3.761 | 22.8 | 0.56 | -1.13 | 10.756 | 35 | 11.951 | 31.5
L26 | B17 | B27 | L26 | Line | 345 | 116 | -97.67 | -57.11 | 113.14 | -86.3 | 1.158 | 148.2 | 0.15 | -28.96 | 4.78 | 24.2 | 7.171 | 16.1
L17 | B10 | B13 | L17 | Line | 345 | 28.8 | 302.85 | 48.45 | 306.7 | 98.7 | 3.1 | -8.3 | 0.39 | -2.96 | 10.756 | 28.8 | 11.951 | 25.9
L27 | B21 | B22 | L27 | Line | 345 | 93.8 | -185.16 | -120.61 | 220.98 | -83.8 | 2.288 | 145.4 | 0.4 | -17.46 | 7.971 | 28.7 | 11.951 | 19.1
L18 | B13 | B14 | L18 | Line | 345 | 67.7 | 296.28 | 15.88 | 296.7 | 99.9 | 3.009 | -3 | 0.82 | -7.49 | 10.756 | 28 | 11.951 | 25.2
L28 | B22 | B23 | L28 | Line | 345 | 64.3 | 461.81 | 300.42 | 550.93 | 83.8 | 5.601 | -33.1 | 1.91 | 13.37 | 7.171 | 78.1 | 9.561 | 58.6
L19 | B14 | B15 | L19 | Line | 345 | 145.4 | 54.67 | 81.53 | 98.16 | 55.7 | 1 | -57.9 | 0.24 | -31.54 | 4.78 | 20.9 | 7.171 | 14
L29 | B23 | B24 | L29 | Line | 345 | 234.6 | -29.96 | -57.26 | 64.63 | -46.4 | 0.679 | 115 | 0.06 | -32.24 | 4.78 | 14.2 | 7.171 | 9.5
L1 | B1 | B2 | L1 | Line | 345 | 275.5 | -376.89 | 92.39 | 388.05 | -97.1 | 3.818 | -168.5 | 5.37 | -57.68 | 10.756 | 35.5 | 11.951 | 31.9
L2 | B1 | B39 | L2 | Line | 345 | 167.6 | 376.89 | -92.4 | 388.05 | 97.1 | 3.818 | 11.5 | 1.4 | -43.44 | 10.756 | 35.5 | 11.951 | 31.9
L3 | B2 | B3 | L3 | Line | 345 | 101.2 | 341.7 | 114.69 | 360.43 | 94.8 | 3.541 | -18.6 | 1.67 | -6.69 | 4.78 | 74.1 | 7.171 | 49.4
L4 | B2 | B25 | L4 | Line | 345 | 57.6 | -417.11 | 183.51 | 455.7 | -91.5 | 4.476 | -156.3 | 14.21 | 2.13 | 4.78 | 93.6 | 7.171 | 62.4
L5 | B3 | B4 | L5 | Line | 345 | 142.8 | 61.24 | 28.99 | 67.75 | 90.4 | 0.68 | -28.2 | 0.07 | -20.61 | 4.78 | 14.2 | 7.171 | 9.5
L6 | B3 | B18 | L6 | Line | 345 | 89.1 | -43.21 | 89.99 | 99.83 | -43.3 | 1.002 | -118.5 | 0.13 | -19.32 | 4.78 | 21 | 7.171 | 14
L7 | B4 | B5 | L7 | Line | 345 | 85.8 | -198.54 | -187.31 | 272.96 | -72.7 | 2.767 | 133.1 | 0.59 | -3.92 | 10.756 | 25.7 | 11.951 | 23.1
L8 | B4 | B14 | L8 | Line | 345 | 86.5 | -240.29 | 52.91 | 246.05 | -97.7 | 2.494 | -171.2 | 0.5 | -5.26 | 4.78 | 52.2 | 7.171 | 34.8
L9 | B5 | B6 | L9 | Line | 345 | 17.4 | -271.73 | 198.31 | 336.4 | -80.8 | 3.324 | -146.1 | 0.22 | -1.53 | 10.756 | 30.9 | 11.951 | 27.8
DC Line Report
ID | Bus From | Bus To | DBase ID | DC Current | DC Power Losses | Commut. X (Rectifier) | Commut. X (Inverter) | Alpha | Gamma | Gamma Min | PF (Rectifier) | PF (Inverter) | DC Voltage (Rectifier) | DC Voltage (Inverter) | DC Power (Rectifier) | DC Power (Inverter) | AC Volt (Rectifier) | AC Volt (Inverter) | P to Converter (Rectifier) | Q to Converter (Rectifier) | P to Converter (Inverter) | Q to Converter (Inverter) | P from Network (Rectifier) | Q from Network (Rectifier) | P from Network (Inverter) | Q from Network (Inverter)
DC1 | B39_REC | B9_INV | DC1 | 1000 | 1 | 2.83 | 2.83 | 23.7 | 5.28 | 10 | 0.93 | 0.96 | 500 | 499 | 501 | 500 | 102 | 94 | 501 | 176 | -500 | 117 | 502 | 195 | -499 | 139
Transformer
TXFO ID | Bus From | Bus To | DBase ID | Type | Rated S [MVA] | kV Nominal Primary | kV Nominal Secondary | P [MW] | Q [MVAR] | S [MVA] | P. Factor [%] | I [pu] | Iangle [deg] | P losses [MW] | Q losses [MVAR] | Capacity (Norm.) [MVA] | Loading [%] Capacity | Capacity (Emer.) [MVA] | Loading [%] Capacity | Tap Ratio % | Tap Pos [%] | Min | Max | Setpoint Min | Setpoint Max | Ctrld Bus/V [pu] | Ctrled BusID
Tap Pos [%]
T10 | B2 | B30 | T10 | Fixed-Tap Xmer | 1000 | 345 | 16.5 | -306.84 | -148.13 | 340.72 | -90.1 | 3.347 | 154.2 | 0.67 | 20.28 | 1100 | 31 | 1150 | 29.6 | 100 | 100
T01 | B12 | B11 | T01 | Fixed-Tap Xmer | 300 | 138 | 345 | -1.33 | -53.05 | 53.06 | -2.5 | 0.547 | 91.3 | 0.05 | 1.3 | 500 | 10.6 | 550 | 9.6 | 100 | 100
T11 | B29 | B38 | T11 | Fixed-Tap Xmer | 1000 | 345 | 16.5 | -1012.9 | 33.24 | 1013.45 | -99.9 | 10.018 | -165.4 | 8.03 | 156.56 | 1100 | 92.1 | 1150 | 88.1 | 100 | 100
T02 | B12 | B13 | T02 | Fixed-Tap Xmer | 300 | 138 | 345 | -6.17 | -34.95 | 35.49 | -17.4 | 0.366 | 99.9 | 0.02 | 0.58 | 500 | 7.1 | 550 | 6.5 | 100 | 100
T12 | B19 | B20 | T12 | Fixed-Tap Xmer | 1000 | 345 | 230 | -377.17 | 37.55 | 379.04 | -99.5 | 3.904 | -161.3 | 1.07 | 21.04 | 1100 | 34.5 | 1150 | 33 | 100 | 100
T03 | B6 | B31 | T03 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -121.26 | 107.3 | 161.92 | -74.9 | 1.607 | -140.3 | 0.17 | 6.46 | 800 | 20.2 | 850 | 19 | 100 | 100
T04 | B10 | B32 | T04 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -647.81 | 90.94 | 654.17 | -99 | 6.612 | -171.2 | 2.19 | 87.41 | 900 | 72.7 | 950 | 68.9 | 100 | 100
T05 | B19 | B33 | T05 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -772.87 | -99.03 | 779.19 | -99.2 | 8.026 | -174.3 | 4.51 | 91.44 | 900 | 86.6 | 950 | 82 | 100 | 100
T06 | B20 | B34 | T06 | Fixed-Tap Xmer | 600 | 230 | 16.5 | -1006.24 | -86.49 | 1009.95 | -99.6 | 10.415 | -168.8 | 9.76 | 195.19 | 1400 | 72.1 | 1500 | 67.3 | 100 | 100
T07 | B22 | B35 | T07 | Fixed-Tap Xmer | 800 | 345 | 16.5 | -647.37 | -403.56 | 762.85 | -84.9 | 7.756 | 148 | 2.63 | 86.05 | 900 | 84.8 | 950 | 80.3 | 100 | 100
T08 | B23 | B36 | T08 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -557.64 | -340.28 | 653.27 | -85.4 | 6.865 | 146 | 2.36 | 128.17 | 800 | 81.7 | 850 | 76.9 | 100 | 100
T09 | B25 | B37 | T09 | Fixed-Tap Xmer | 700 | 345 | 16.5 | -661.71 | 82.67 | 666.86 | -99.2 | 6.464 | -170.2 | 2.51 | 96.96 | 800 | 83.4 | 850 | 78.5 | 100 | 100
[21 empty] | Tap Pos [%] | Min Tap [%] | Max Tap [%] | Bus Min V [pu] | Bus Max V [pu]
T_REC | B39 | B39_REC | T_REC | Tcul Xmer | 800 | 345 | 100 | 501.52 | 195.18 | 538.16 | 93.2 | 5.225 | -28.7 | 0.52 | 19.31 | 1100 | 48.9 | 1200 | 44.8 | 100 | 100 | 90 | 110 | 3.45 | 3.45 | 3.45 | B39_REC
T_INV | B9 | B9_INV | T_INV | Tcul Xmer | 800 | 345 | 100 | -499.44 | 138.53 | 518.29 | -96.4 | 5.464 | -156 | 0.56 | 21.11 | 1100 | 47.1 | 1200 | 43.2 | 100 | 100 | 90 | 110 | 3.45 | 3.45 | 3.45 | B9_INV
Abnormal Report
ID
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L10 | B5 | B8 | 1.061 | 2.39
L20 | B15 | B16 | 2.802 | 5.378
L30 | B25 | B26 | 0.503 | 2.39
L11 | B6 | B7 | 2.137 | 2.39
L21 | B16 | B17 | 1.933 | 5.378
L12 | B6 | B11 | 3.89 | 5.378
L32 | B26 | B28 | 2.311 | 2.39
L13 | B7 | B8 | 2.87 | 5.378
L23 | B16 | B21 | 0.967 | 2.39
L14 | B8 | B9 | 5.341 | 5.378
L25 | B17 | B18 | 2.251 | 2.39
L16 | B10 | B11 | 3.761 | 5.378
L26 | B17 | B27 | 1.158 | 2.39
L17 | B10 | B13 | 3.1 | 5.378
L27 | B21 | B22 | 2.288 | 3.986
L18 | B13 | B14 | 3.009 | 5.378
L19 | B14 | B15 | 1 | 2.39
L29 | B23 | B24 | 0.679 | 2.39
L1 | B1 | B2 | 3.818 | 5.378
L2 | B1 | B39 | 3.818 | 5.378
L5 | B3 | B4 | 0.68 | 2.39
L6 | B3 | B18 | 1.002 | 2.39
L7 | B4 | B5 | 2.767 | 5.378
L9 | B5 | B6 | 3.324 | 5.378
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B2 | B30 | 340.723 | 550
T01 | B12 | B11 | 53.063 | 250
T02 | B12 | B13 | 35.494 | 250
T12 | B19 | B20 | 379.039 | 550
T03 | B6 | B31 | 161.919 | 400
T_REC | B39 | B39_REC | 538.163 | 550
T_INV | B9 | B9_INV | 518.295 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]
Summary Report
LOAD FLOW STUDY PARAMETERS
Study : |  |  | UNTITLED
Time : |  |  | Fri Jul 23 12h58m22s 2021
Method : |  |  | Newton-Raphson
Constraints : |  |  | Not applied
Flat start : |  |  | Yes
Tcul txfo used as fixed tap : |  |  | Yes
Block Q-flow Txfo Adjustment |  |  | n\a
Block P-flow Txfo Adjustment : |  |  | n\a
Block Switchable Shunt Adjustment : |  |  | n\a
Block DC Link Adjustment : |  |  | No
Base power : |  |  | 100.00 [MVA]
Tolerance : |  |  | 0.100 [MVA]
COMPLETE SUMMARY REPORT
Summary Data |  |  |  |  | Active Power |  | Reactive Power
Total generation |  |  |  |  | 7006.697 |  | 1051.201
Spinning reserve |  |  |  |  | 8383.303
Static Load |  |  |  |  | 6097.1 |  | 1408.9
Shunt loads |  |  |  |  | 0 |  | -2003.696
Motor loads |  |  |  |  | 800 |  | 600
Total load |  |  |  |  | 6897.1 |  | 5.204
Line / cable losses |  |  |  |  | 73.569 |  | -179.146
Transformer losses |  |  |  |  | 35.031 |  | 931.859
Total losses |  |  |  |  | 109.6 |  | 1045.712
Mismatches |  |  |  |  | -0.003 |  | 0.285